## Vic
Location and network constraint information:
Display name | Wemen TS | KGTS-SHL line | Wangaratta ZS | NKA-CME line | Boundary Bend ZS | Ballarat TS | Cobram East ZS | Merbein ZS | Eaglehawke ZS | Bendigo TS | Maryborough ZS | Bendigo ZS | Thomastown ZS | KTS-MLN line | Melton ZS | Sale ZS | Bacchus Marsh ZS | Keilor TS | Watsonia ZS | Werribee ZS | Epping ZS | Ferntree Gully ZS | St Albans ZS | Warragul ZS | Bairnsdale ZS | BLTS-BMH line | Geelong East ZS | Swan Hill ZS | Numurkah ZS | Lang Lang ZS | Myrtleford ZS | WPD-TQY line | MWTS-LGA-FTR line | DPTS-MLN line | SMTS-KLO line | Torquay ZS | RWTS-BRA-BWR line | TTS-NEI-NH-WT line
Short name | WETS | KGTS-SHL | WN | NKA-CME | BBD | BATS | CME | MBN | EHK | BETS | MRO | BGO | TT | KTS-MLN | MLN | SLE | BMH | KTS | WT | WBE | EPG | FGY | SA | WGL | BDL | BLTS-BMH | GLE | SHL | NKA | LLG | MYT | WPD-TQY | MWTS-LGA-FTR-MWTS | DPTS-MLN | SMTS-KLO | TQY | RWTS-BRA-BWR-RWTS | TTS-NEI-NH-WT-TTS
Full name | Wemen TS | Kerang TS - Swan Hill ZS StLi #1 Circuit | Wangaratta | Numurkah ZS - Cobram East ZS StLi 66kV | Boundary Bend ZS 22kV | Ballarat TS 66kV | Cobram East ZS 22kV | Merbein ZS 22kV | Eaglehawke ZS 22kV | Bendigo TS 66kV and 22kV | Maryborough ZS 22kV | Bendigo ZS 22kV | Thomastown | Keilor TS - Melton ZS StLi Circuit 66kV | Melton ZS 22kV | Sale | Bacchus Marsh ZS 22kV | Keilor TS | Watsonia | Werribee ZS 22kV | Epping | Ferntree Gully | St Albans ZS 22kV | Warragul | Bairnsdale | Brooklyn TS - Bacchus Marsh ZS StLi Circuit 66kV | Geelong East ZS 22kV | Swan Hill ZS 22kV | Numurkah ZS | Lang Lang | Myrtleford | Waurn Ponds ZS - Torquay ZS StLi | Morwell TS - Leongatha ZS - Foster ZS Circuit | Deer Park TS - Melton ZS StLi 66kV | South Morang TS - Kalkallo ZS Radial Line | Torquay ZS | Ringwood TS - Boronia ZS - Bayswater ZS Circuit | Thomastown TS - Nilsens ZS - North Heidelberg ZS - Watsonia ZS Circuit
Provider | Powercor | Powercor | SPAusnet | Powercor | Powercor | Powercor | Powercor | Powercor | Powercor | Powercor | Powercor | Powercor | SPAusnet | Powercor | Powercor | SPAusnet | Powercor | Powercor | SPAusnet | Powercor | SPAusnet | SPAusnet | Powercor | SPAusnet | SPAusnet | Powercor | Powercor | Powercor | Powercor | SPAusnet | SPAusnet | Powercor | SPAusnet | Powercor | SPAusnet | Powercor | SPAusnet | SPAusnet
Latitude | -34.7868 | -35.3468 | -36.3645 | -35.9721 | -34.717 | -37.569 | -35.9721 | -34.1763 | -36.7374 | -36.7865 | -37.051 | -36.7721 | -37.6909 | -37.6888 | -37.6888 | -38.1014 | -37.7011 | -37.7397 | -37.7134 | -37.892 | -37.6526 | -37.8935 | -37.7416 | -38.1538 | -37.8084 | -37.7011 | -38.1812 | -35.3468 | -36.0709 | -38.2674 | -36.5652 | -38.3147 | -38.4735 | -37.6888 | -37.6525 | -38.3147 | -37.7635 | -37.7134
Longitude | 142.5251 | 143.5213 | 146.3143 | 145.6953 | 143.1517 | 143.9205 | 145.6953 | 142.0782 | 144.2773 | 144.2527 | 143.7534 | 144.276 | 145.0108 | 144.5846 | 144.5846 | 147.0957 | 144.407 | 144.8448 | 145.0857 | 144.6615 | 145.0261 | 145.2924 | 144.8239 | 145.9427 | 147.6477 | 144.407 | 144.3801 | 143.5213 | 145.4499 | 145.5566 | 146.7033 | 144.3238 | 145.9472 | 144.5846 | 145.0263 | 144.3238 | 145.3581 | 145.0857
Proposed network investment ($m) | 12 | 4.1 | 4.5 | 11 | 4 | 15.5 | 1.7 | 3 | 6 | 28 | 4 | 1 | 6 | 6.2 | 3.6 | 5 | 0.8 | 147 | - | 15 | - | 6 | 0.2 | 6 | 6 | 8 | 10 | - | - | 3.5 | 0.5 | 1.4 | 6.5 | 17.6 | 13.5 | 11.64 | 3.4 | 2.2
Annual network support payment ($m/yr) | 0.88312 | 0.30173 | 0.33117 | 0.80953 | 0.29437 | 1.1407 | 0.12511 | 0.22078 | 0.44156 | 2.0606 | 0.29437 | 0.073594 | 0.44156 | 0.45628 | 0.26494 | 0.36797 | 0.058875 | [8 empty] | 0.58875
Commissioning year | 2021 | 2016 | 2018 | 2017 | 2015 | 2022 | 2017 | 2015 | 2016 | 2014 | 2019 | 2014 | 2019 | 2017 | 2016 | 2015 | 2014 | 2018 | - | 2015 | - | 2018 | 2015 | 2019 | 2015 | 2015 | 2015 | - | - | 2018 | 2014 | 2016 | 2017 | 2015 | 2016 | 2016 | 2014 | 2014
Maximum connection (MW) | 77 | 58.2 | 66 | 44.9 | 33 | 341 | 40.5 | 26 | 54 | 350 | 27 | 66 | 84 | 112.5 | 66 | 39.5 | 27 | 509 | 109 | 99 | 99 | 93 | 93 | 84 | 48 | 47.4667 | 40.5 | 40.5 | 39.5 | 19.9 | 18.8 | - | - | - | - | - | - | -
Maximum constraint (MVA) | 15.3 | 24.2 | 3.74 | 7.7 | 11.1133 | 37.6111 | 7.04 | 19.2867 | 28.21 | 71.03 | 6.16 | 39.2 | 30.14 | 34.65 | 52.365 | 5.26 | 25.18 | 212.6667 | - | 63.6733 | - | 20.68 | 38.0133 | 30.58 | - | 60.8333 | 30.82 | - | - | 5.5 | 1.1 | - | - | - | - | - | - | -
Constraint type | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | None | None | Growth, None | Growth, None
Constraint time for analysis | SA | SE | SE | SE | SE | SE | SE | SE | SE | SE | SE | SE | SE | SE | SE | SA | SE | SE | WE | SE | WE | SE | SE | WA | SE | SE | SE | WE | WE | WE | WE | WE | WE | WE | WE | WE | WE | WE
Max firm capacity | 90.8% | 90.3% | 89.1% | 91.2% | 90.5% | 80.9% | 91.2% | 90.7% | 82.7% | 82.6% | 80.9% | 82.7% | 81.8% | 80.9% | 80.9% | 86.4% | 82% | 78.4% | 85.5% | 70% | 86.5% | 81.9% | 78.4% | 89.3% | 80.8% | 82% | 63.1% | 88.5% | 94.6% | 79.7% | 79.7% | 59.5% | 84.9% | 82.5% | 86.5% | 59.5% | 80.9% | 85.5%
DNI (MJ/m2/yr) | 23.443 | 22.9315 | 21.1011 | 21.6582 | 23.6149 | 17.1649 | 21.6582 | 24.122 | 20.8357 | 20.6178 | 19.699 | 20.6771 | 15.3425 | 15.7719 | 15.7719 | 15.7199 | 15.4686 |  | 15.1375 |  | 15.4328 | 13.5 |  | 13.5 | 15.3372 | 15.4686 |  | 22.9315 | 21.7225 |  |  |  | 13.5 | 15.7719 | 15.4317 |  | 13.5 | 15.1375
Calculated on | SA: TS; SE: Stli; SE: ZS; SE: Stli; SE: ZS; SE: TS; SE: ZS; SE: ZS; SE: ZS; SE: TS; SE: ZS; SE: ZS; SE: ZS; SE: Stli; SE: ZS; SA: ZS; SE: ZS
Reason for exclusion | SE: Firm Capacity too low: 0.784; WE: Asset: Insufficient information; SE: Firm Capacity too low: 0.7; WE: Asset: Insufficient information; SE: DNI too low: 13.5; SE: Firm Capacity too low: 0.784; WA: DNI too low: 13.5; SE: Asset: Insufficient information; SE: Asset: No plant configuration can meet the constraint; SE: Firm Capacity too low: 0.631; WE: Asset: Insufficient information; WE: Asset: Insufficient information; WE: Firm Capacity too low: 0.797; WE: Firm Capacity too low: 0.797; WE: Firm Capacity too low: 0.595; WE: DNI too low: 13.5; WE: Asset: Insufficient information; WE: Asset: Insufficient information; WE: Firm Capacity too low: 0.595; WE: DNI too low: 13.5; WE: Asset: Insufficient information
Warnings |  | No hourly data |  | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | Recorded peak in Morning | No hourly data | No hourly data |  | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data |  | No hourly data |  |  | No hourly data | No hourly data | No hourly data | No hourly data |  | Recorded peak in Morning | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data
Optimal plant
Plant size (MW) | SA: 77; SE: 58.2; SE: 66; SE: 44.9; SE: 33; SE: 120; SE: 38; SE: 26; SE: 54; SE: 120; SE: 27; SE: 66; SE: 84; SE: 112.5; SE: 66; SA: 39.5; SE: 27
Storage (hours) | SA: 5; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SA: 15; SE: 15
Firm Capacity (%) | SA: 85.6%; SE: 90.3%; SE: 89.1%; SE: 91.2%; SE: 90.5%; SE: 80.9%; SE: 91.2%; SE: 90.7%; SE: 82.7%; SE: 82.6%; SE: 80.9%; SE: 82.7%; SE: 81.8%; SE: 80.9%; SE: 80.9%; SA: 86.4%; SE: 82%
Connection costs component to total plant costs ($m) | SA: 35.0721; SE: 31.0433; SE: 32.7148; SE: 28.1931; SE: 25.6429; SE: 44.287; SE: 26.7144; SE: 24.1428; SE: 30.1432; SE: 44.287; SE: 24.3571; SE: 32.7148; SE: 36.5722; SE: 42.6798; SE: 32.7148; SA: 27.0359; SE: 24.3571
Total plant cost (including connection costs) ($m) | SA: 416.0001; SE: 550.2496; SE: 565.8554; SE: 421.0812; SE: 355.7725; SE: 806.2985; SE: 360.5678; SE: 304.4437; SE: 515.0026; SE: 1156.5851; SE: 264.8357; SE: 665.6105; SE: 673.1294; SE: 964.7468; SE: 615.7082; SA: 400.5206; SE: 323.822
Cost per MW ($m/MW) | SA: 4.9471; SE: 8.9211; SE: 8.0779; SE: 8.7503; SE: 10.0039; SE: 6.3501; SE: 8.7856; SE: 10.7808; SE: 8.9789; SE: 9.2692; SE: 8.9066; SE: 9.5893; SE: 7.5781; SE: 8.1962; SE: 8.8332; SA: 9.4553; SE: 11.0913
Capacity factor (%) | SA: 43.28%; SE: 59.99%; SE: 50.14%; SE: 52.95%; SE: 64.14%; SE: 34.09%; SE: 52.95%; SE: 67.41%; SE: 48.85%; SE: 47.82%; SE: 43.7%; SE: 48.1%; SE: 28.52%; SE: 29.74%; SE: 29.74%; SA: 29.59%; SE: 28.87%
Annual generation (MWh) | SA: 291902.1939; SE: 305843.3924; SE: 289880.7382; SE: 208271.9431; SE: 185428.167; SE: 358366.2102; SE: 176265.787; SE: 153539.2124; SE: 231085.0411; SE: 502675.2927; SE: 103362.1164; SE: 278080.7406; SE: 209827.9285; SE: 293096.9287; SE: 171950.1982; SA: 102386.5842; SE: 68283.4477
Max connection distance (km) | SA: 15.4; SE: 11.64; SE: 13.2; SE: 8.98; SE: 6.6; SE: 24; SE: 7.6; SE: 5.2; SE: 10.8; SE: 24; SE: 5.4; SE: 13.2; SE: 16.8; SE: 22.5; SE: 13.2; SA: 7.9; SE: 5.4
Area required (ha) | SA: 371.7889; SE: 455.8088; SE: 509.1866; SE: 361.9606; SE: 274.9647; SE: 845.0467; SE: 311.8658; SE: 222.4555; SE: 426.5582; SE: 845.0467; SE: 230.0174; SE: 509.1866; SE: 627.6796; SE: 801.919; SE: 509.1866; SA: 322.8377; SE: 230.0174
O&M ($/mWh) | SA: 12.7988; SE: 17.3046; SE: 15.3949; SE: 17.533; SE: 20.4325; SE: 10.9837; SE: 18.1855; SE: 21.5276; SE: 17.5908; SE: 16.0327; SE: 17.8488; SE: 18.2754; SE: 13.9207; SE: 14.3382; SE: 16.8345; SA: 19.6436; SE: 22.2269
Annual network support payment ($m/yr) | SA: 0.88312; SE: 0.30173; SE: 0.33117; SE: 0.80953; SE: 0.29437; SE: 1.1407; SE: 0.12511; SE: 0.22078; SE: 0.44156; SE: 2.0606; SE: 0.29437; SE: 0.073594; SE: 0.44156; SE: 0.45628; SE: 0.26494; SA: 0.36797; SE: 0.058875; SE: 0.58875
Cost gap calculation
LCOE ($) | SA: 133.511; SE: 174.336; SE: 185.5199; SE: 192.0283; SE: 185.1176; SE: 207.6727; SE: 193.3852; SE: 190.397; SE: 211.6748; SE: 220.7146; SE: 233.0579; SE: 228.802; SE: 294.5415; SE: 305.3408; SE: 330.4565; SA: 357.0672; SE: 427.8999
Electricity sales (ex. carbon price effect) ($) | SA: 72.7989; SE: 46.2328; SE: 53.8122; SE: 49.5482; SE: 45.4664; SE: 72.2969; SE: 49.5482; SE: 45.4664; SE: 46.2328; SE: 45.4195; SE: 58.1577; SE: 45.4195; SE: 58.1577; SE: 49.5482; SE: 46.2328; SA: 45.4664; SE: 45.4195
Carbon price effect ($) | SA: 53.4686; SE: 27.8678; SE: 35.7208; SE: 31.992; SE: 22.3712; SE: 52.8379; SE: 31.992; SE: 22.3712; SE: 27.8678; SE: 17.372; SE: 40.2319; SE: 17.372; SE: 40.2319; SE: 31.992; SE: 27.8678; SA: 22.3712; SE: 17.372
LRET ($) | SA: 21.7925; SE: 50.5596; SE: 40.5045; SE: 45.8896; SE: 54.4639; SE: 15.5953; SE: 45.8896; SE: 54.4639; SE: 50.5596; SE: 57.1779; SE: 34.5705; SE: 57.1779; SE: 34.5705; SE: 45.8896; SE: 50.5596; SA: 54.4639; SE: 57.1779
NSP contribution to LCOE ($/MWh) | SA: 3.0254; SE: 0.98656; SE: 1.1424; SE: 3.8869; SE: 1.5875; SE: 3.1831; SE: 0.70978; SE: 1.4379; SE: 1.9108; SE: 4.0993; SE: 2.848; SE: 0.26465; SE: 2.1044; SE: 1.5568; SE: 1.5408; SA: 3.5939; SE: 0.86221
NET BENEFIT OR LOSS ($/MWh) | SA: 17.5744; SE: -48.6892; SE: -54.34; SE: -60.7116; SE: -61.2287; SE: -63.7596; SE: -65.2456; SE: -66.6577; SE: -85.1037; SE: -96.6459; SE: -97.2499; SE: -108.568; SE: -159.477; SE: -176.3543; SE: -204.2555; SA: -231.1719; SE: -307.0683
Smallest viable plant size:
Plant size (MW) | SA: 15.3; SE: 24.2; SE: 3.74; SE: 7.7; SE: 11.1133; SE: 37.6111; SE: 7.04; SE: 19.2867; SE: 28.21; SE: 71.03; SE: 6.16; SE: 39.2; SE: 30.14; SE: 34.65; SE: 52.365; SA: 5.26; SE: 25.18
Storage (hours) | SA: 10; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SA: 15; SE: 15
Firm Capacity (%) | SA: 90.7%; SE: 90.3%; SE: 89.1%; SE: 91.2%; SE: 90.5%; SE: 80.9%; SE: 91.2%; SE: 90.7%; SE: 82.7%; SE: 82.6%; SE: 80.9%; SE: 82.7%; SE: 81.8%; SE: 80.9%; SE: 80.9%; SA: 86.4%; SE: 82%
Connection costs component to total plant costs ($m) | SA: 10.8406; SE: 12.8251; SE: 4.7433; SE: 7.8688; SE: 9.4569; SE: 26.6311; SE: 7.481; SE: 11.8428; SE: 24.6164; SE: 33.7927; SE: 6.903; SE: 26.9716; SE: 25.03; SE: 25.9965; SE: 29.7928; SA: 6.2194; SE: 23.9671
Total plant cost (including connection costs) ($m) | SA: 143.9599; SE: 268.7101; SE: 69.7073; SE: 119.4906; SE: 165.8765; SE: 284.1924; SE: 112.4447; SE: 240.1925; SE: 308.8949; SE: 711.3439; SE: 94.1239; SE: 413.7597; SE: 284.3688; SE: 339.3602; SE: 501.2815; SA: 99.8334; SE: 309.4272
Cost per MW ($m/MW) | SA: 8.7006; SE: 10.5738; SE: 17.37; SE: 14.4963; SE: 14.075; SE: 6.848; SE: 14.9096; SE: 11.8398; SE: 10.0772; SE: 9.5389; SE: 14.1592; SE: 9.867; SE: 8.6045; SE: 9.0437; SE: 9.0039; SA: 17.7973; SE: 11.3368
Capacity factor (%) | SA: 55.61%; SE: 59.99%; SE: 50.14%; SE: 52.95%; SE: 64.14%; SE: 34.09%; SE: 52.95%; SE: 67.41%; SE: 48.85%; SE: 47.82%; SE: 43.7%; SE: 48.1%; SE: 28.52%; SE: 29.74%; SE: 29.74%; SA: 29.59%; SE: 28.87%
Annual generation (MWh) | SA: 74535.0618; SE: 127171.9948; SE: 16426.5752; SE: 35717.0147; SE: 62446.213; SE: 112321.2612; SE: 32655.5563; SE: 113894.6004; SE: 120720.5372; SE: 297541.8837; SE: 23581.8755; SE: 165163.1065; SE: 75288.2591; SE: 90273.854; SE: 136426.8504; SA: 13634.2641; SE: 63680.6375
Max connection distance (km) | SA: 3.06; SE: 4.84; SE: 0.748; SE: 1.54; SE: 2.2227; SE: 7.5222; SE: 1.408; SE: 3.8573; SE: 5.642; SE: 14.206; SE: 1.232; SE: 7.84; SE: 6.028; SE: 6.93; SE: 10.473; SA: 1.052; SE: 5.036
Area required (ha) | SA: 117.7371; SE: 208.7933; SE: 48.9031; SE: 80.509; SE: 107.4978; SE: 309.0138; SE: 75.2633; SE: 171.1676; SE: 239.1403; SE: 542.9572; SE: 68.2554; SE: 320.6469; SE: 253.6305; SE: 287.1978; SE: 415.0751; SA: 61.0721; SE: 216.2397
O&M ($/mWh) | SA: 18.2333; SE: 20.9712; SE: 28.8668; SE: 25.7962; SE: 25.932; SE: 14.161; SE: 26.3075; SE: 22.9829; SE: 20.2787; SE: 17.9838; SE: 24.6695; SE: 20.4842; SE: 17.4239; SE: 18.5568; SE: 17.7096; SA: 30.5478; SE: 22.5692
Annual network support payment ($m/yr) | SA: 0.88312; SE: 0.30173; SE: 0.33117; SE: 0.80953; SE: 0.29437; SE: 1.1407; SE: 0.12511; SE: 0.22078; SE: 0.44156; SE: 2.0606; SE: 0.29437; SE: 0.073594; SE: 0.44156; SE: 0.45628; SE: 0.26494; SA: 0.36797; SE: 0.058875; SE: 0.58875
Cost gap calculation
LCOE ($) | SA: 183.4393; SE: 207.0938; SE: 394.6898; SE: 314.8771; SE: 257.6345; SE: 226.2726; SE: 323.6301; SE: 208.4397; SE: 238.1042; SE: 228.6232; SE: 366.797; SE: 237.1078; SE: 336.0533; SE: 339.6509; SE: 337.3908; SA: 665.6663; SE: 437.2212
Electricity sales (ex. carbon price effect) ($) | SA: 70.0929; SE: 46.2328; SE: 53.8122; SE: 49.5482; SE: 45.4664; SE: 72.2969; SE: 49.5482; SE: 45.4664; SE: 46.2328; SE: 45.4195; SE: 58.1577; SE: 45.4195; SE: 58.1577; SE: 49.5482; SE: 46.2328; SA: 45.4664; SE: 45.4195
Carbon price effect ($) | SA: 51.481; SE: 27.8678; SE: 35.7208; SE: 31.992; SE: 22.3712; SE: 52.8379; SE: 31.992; SE: 22.3712; SE: 27.8678; SE: 17.372; SE: 40.2319; SE: 17.372; SE: 40.2319; SE: 31.992; SE: 27.8678; SA: 22.3712; SE: 17.372
LRET ($) | SA: 21.7925; SE: 50.5596; SE: 40.5045; SE: 45.8896; SE: 54.4639; SE: 15.5953; SE: 45.8896; SE: 54.4639; SE: 50.5596; SE: 57.1779; SE: 34.5705; SE: 57.1779; SE: 34.5705; SE: 45.8896; SE: 50.5596; SA: 54.4639; SE: 57.1779
NSP contribution to LCOE ($/MWh) | SA: 11.8484; SE: 2.3726; SE: 20.1607; SE: 22.6651; SE: 4.7141; SE: 10.1557; SE: 3.8312; SE: 1.9385; SE: 3.6577; SE: 6.9255; SE: 12.4831; SE: 0.44558; SE: 5.865; SE: 5.0544; SE: 1.942; SA: 26.9885; SE: 0.92453
NET BENEFIT OR LOSS ($/MWh) | SA: -28.2245; SE: -80.0609; SE: -244.4916; SE: -164.7822; SE: -130.6191; SE: -75.3868; SE: -192.3691; SE: -84.1998; SE: -109.7862; SE: -101.7284; SE: -221.3539; SE: -116.6928; SE: -197.2283; SE: -207.1666; SE: -210.7886; SA: -516.3764; SE: -316.3273
Largest viable plant size:
Plant size (MW) | SA: 77; SE: 58.2; SE: 66; SE: 44.9; SE: 33; SE: 120; SE: 40.5; SE: 26; SE: 54; SE: 120; SE: 27; SE: 66; SE: 84; SE: 112.5; SE: 66; SA: 39.5; SE: 27
Storage (hours) | SA: 5; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SE: 15; SA: 15; SE: 15
Firm Capacity (%) | SA: 85.6%; SE: 90.3%; SE: 89.1%; SE: 91.2%; SE: 90.5%; SE: 80.9%; SE: 91.2%; SE: 90.7%; SE: 82.7%; SE: 82.6%; SE: 80.9%; SE: 82.7%; SE: 81.8%; SE: 80.9%; SE: 80.9%; SA: 86.4%; SE: 82%
Connection costs component to total plant costs ($m) | SA: 35.0721; SE: 31.0433; SE: 32.7148; SE: 28.1931; SE: 25.6429; SE: 44.287; SE: 27.2502; SE: 24.1428; SE: 30.1432; SE: 44.287; SE: 24.3571; SE: 32.7148; SE: 36.5722; SE: 42.6798; SE: 32.7148; SA: 27.0359; SE: 24.3571
Total plant cost (including connection costs) ($m) | SA: 416.0001; SE: 550.2496; SE: 565.8554; SE: 421.0812; SE: 355.7725; SE: 806.2985; SE: 385.6946; SE: 304.4437; SE: 515.0026; SE: 1156.5851; SE: 264.8357; SE: 665.6105; SE: 673.1294; SE: 964.7468; SE: 615.7082; SA: 400.5206; SE: 323.822
Cost per MW ($m/MW) | SA: 4.9471; SE: 8.9211; SE: 8.0779; SE: 8.7503; SE: 10.0039; SE: 6.3501; SE: 8.8505; SE: 10.7808; SE: 8.9789; SE: 9.2692; SE: 8.9066; SE: 9.5893; SE: 7.5781; SE: 8.1962; SE: 8.8332; SA: 9.4553; SE: 11.0913
Capacity factor (%) | SA: 43.28%; SE: 59.99%; SE: 50.14%; SE: 52.95%; SE: 64.14%; SE: 34.09%; SE: 52.95%; SE: 67.41%; SE: 48.85%; SE: 47.82%; SE: 43.7%; SE: 48.1%; SE: 28.52%; SE: 29.74%; SE: 29.74%; SA: 29.59%; SE: 28.87%
Annual generation (MWh) | SA: 291902.1939; SE: 305843.3924; SE: 289880.7382; SE: 208271.9431; SE: 185428.167; SE: 358366.2102; SE: 187862.2204; SE: 153539.2124; SE: 231085.0411; SE: 502675.2927; SE: 103362.1164; SE: 278080.7406; SE: 209827.9285; SE: 293096.9287; SE: 171950.1982; SA: 102386.5842; SE: 68283.4477
Max connection distance (km) | SA: 15.4; SE: 11.64; SE: 13.2; SE: 8.98; SE: 6.6; SE: 24; SE: 8.1; SE: 5.2; SE: 10.8; SE: 24; SE: 5.4; SE: 13.2; SE: 16.8; SE: 22.5; SE: 13.2; SA: 7.9; SE: 5.4
Area required (ha) | SA: 371.7889; SE: 455.8088; SE: 509.1866; SE: 361.9606; SE: 274.9647; SE: 845.0467; SE: 330.1271; SE: 222.4555; SE: 426.5582; SE: 845.0467; SE: 230.0174; SE: 509.1866; SE: 627.6796; SE: 801.919; SE: 509.1866; SA: 322.8377; SE: 230.0174
O&M ($/mWh) | SA: 12.7988; SE: 17.3046; SE: 15.3949; SE: 17.533; SE: 20.4325; SE: 10.9837; SE: 17.9335; SE: 21.5276; SE: 17.5908; SE: 16.0327; SE: 17.8488; SE: 18.2754; SE: 13.9207; SE: 14.3382; SE: 16.8345; SA: 19.6436; SE: 22.2269
Annual network support payment ($m/yr) | SA: 0.88312; SE: 0.30173; SE: 0.33117; SE: 0.80953; SE: 0.29437; SE: 1.1407; SE: 0.12511; SE: 0.22078; SE: 0.44156; SE: 2.0606; SE: 0.29437; SE: 0.073594; SE: 0.44156; SE: 0.45628; SE: 0.26494; SA: 0.36797; SE: 0.058875; SE: 0.58875
Cost gap calculation
LCOE ($) | SA: 133.511; SE: 174.336; SE: 185.5199; SE: 192.0283; SE: 185.1176; SE: 207.6727; SE: 194.4267; SE: 190.397; SE: 211.6748; SE: 220.7146; SE: 233.0579; SE: 228.802; SE: 294.5415; SE: 305.3408; SE: 330.4565; SA: 357.0672; SE: 427.8999
Electricity sales (ex. carbon price effect) ($) | SA: 72.7989; SE: 46.2328; SE: 53.8122; SE: 49.5482; SE: 45.4664; SE: 72.2969; SE: 49.5482; SE: 45.4664; SE: 46.2328; SE: 45.4195; SE: 58.1577; SE: 45.4195; SE: 58.1577; SE: 49.5482; SE: 46.2328; SA: 45.4664; SE: 45.4195
Carbon price effect ($) | SA: 53.4686; SE: 27.8678; SE: 35.7208; SE: 31.992; SE: 22.3712; SE: 52.8379; SE: 31.992; SE: 22.3712; SE: 27.8678; SE: 17.372; SE: 40.2319; SE: 17.372; SE: 40.2319; SE: 31.992; SE: 27.8678; SA: 22.3712; SE: 17.372
LRET ($) | SA: 21.7925; SE: 50.5596; SE: 40.5045; SE: 45.8896; SE: 54.4639; SE: 15.5953; SE: 45.8896; SE: 54.4639; SE: 50.5596; SE: 57.1779; SE: 34.5705; SE: 57.1779; SE: 34.5705; SE: 45.8896; SE: 50.5596; SA: 54.4639; SE: 57.1779
NSP contribution to LCOE ($/MWh) | SA: 3.0254; SE: 0.98656; SE: 1.1424; SE: 3.8869; SE: 1.5875; SE: 3.1831; SE: 0.66596; SE: 1.4379; SE: 1.9108; SE: 4.0993; SE: 2.848; SE: 0.26465; SE: 2.1044; SE: 1.5568; SE: 1.5408; SA: 3.5939; SE: 0.86221
NET BENEFIT OR LOSS ($/MWh) | SA: 17.5744; SE: -48.6892; SE: -54.34; SE: -60.7116; SE: -61.2287; SE: -63.7596; SE: -66.331; SE: -66.6577; SE: -85.1037; SE: -96.6459; SE: -97.2499; SE: -108.568; SE: -159.477; SE: -176.3543; SE: -204.2555; SA: -231.1719; SE: -307.0683
Location and network constraint information:
Max demand (yr 10) | 75.5 | 82.4 | 47.64 | 52.6 | 35.5333 | 246.7889 | 45.6 | 47.8667 | 81.15 | 319.55 | 30.82 | 87.5 | 116.28 | 147.15 | 112.325 | 32.8 | 52.1 | 712.3333 | - | 164.6333 | - | 89.88 | 129.5333 | 95.66 | 44.1 | 108.3 | 78 | - | - | 25.4 | 19.9 | - | - | - | - | - | - | -
Investment trigger point (MW) | 60.2 | 58.2 | 43.9 | 44.9 | 24.42 | 209.1778 | 38.56 | 28.58 | 52.94 | 248.52 | 24.66 | 48.3 | 86.14 | 112.5 | 59.96 | 27.54 | 26.92 | 499.6667 | 109 | 100.96 | 99 | 69.2 | 91.52 | 65.08 | 53.12 | 47.4667 | 47.18 | 36.7 | 30.5 | 19.9 | 18.8 | - | - | - | - | - | - | -
Constraint notes | Wemen TS (WETS)was commissioned in October 2012, with a single 70 MVA transformer. A combination of single transformer outage and load growth could result in unacceptable loss of load. | Reconductor #1 line in stages | Install new 20/33MVA transformer | New #2 line | Additional transformer | New 220/66kV transformer | New 22kV capacitors are expected to be installed after 2017 | Additional 66/22kV transformer | Additional transformer | Install two new 75 MVA 230/22 kV transformers. Value of network investment is given as an annual figure in TCPR. | Additional transformer | Install 22kV feeder from BETS | Install fourth 20/33 MVA transformer by 2016 | Five new 66kV lines | Additional transformer. Investment spread over two years $0.3m in 2014 and $3.2m in 2016. | No.1 Transformer replaced with new 20/33 MVA unit | Augment BMH & MLN 22kV network to increase load transfer away capapcity to adjacent ZS. Additional 22kV feeder at MLN followed by an additional transformer at MLN. | Five 150MVA transformers and four 66kV buses. Note two stages of investment - $6m in 2012/14 for new 100MVAR capacitor bank. In 2015-16, a new $125m TS at Deer Park and associated StLi"s. | Reconductor TTS-WT 66kV line | Establish new Truganina ZS to offload SA, SU, LV, LVN & WBE | New 66kV line | Install a fifth 20/33 transformer in 2015 | Augment 22kV transformer isolators | Install new 20/33 MVA transformer | Install new 20/33 MVA transformer in 2015 | Three investments - $2.4m in 2013, $3.8m in 2014 and $1.4m in 2015, combined and attributed to the year of the largest investment (2014). | Upgrade two transformers |  |  | Install 2nd 20/33 transformer in 2015 | Install transformer cooling fans. Adjust overnight hot water heating load timing. Planned completion <2014 | WPD-TQY line convert 22kV to 66kV. 1st investment of $1.7M in 2013 is assumed to occur, only $1.4M in 2016 included. | Re-conductor 22km of MWTS-LGA No.2 66kV line | Establish two 66kV lines. Deer Park TS will be created to transfer Sunshine ZS from the Keilor TS network to alleviate load at risk at Keilor TS. | KLO-DRN 66kV line | Establish new Torquay ZS (co-ordinates for town) | Construct new CYN-BWR 66kV line | Reconductor TTS-WT 66kV line
Season to use
Constraint | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer |  | Summer |  | Summer | Summer | BOTH (Summer) | Summer | Summer | Summer |  |  | BOTH | Winter
NPV | 11.8155 | 3.4159 | 4.0497 | 9.5444 | 3.1848 | 15.6433 | 1.475 | 2.3886 | 4.9989 | 21.1866 | 3.7204 | 0.75667 | 5.5806 | 5.3796 | 2.9993 | 3.981 | 0.60533 | 132.2914 | - | 11.943 | - | 5.3996 | 0.15924 | 5.5806 | 4.7772 | 6.3696 | 7.962 | - | - | 3.1498 | 0.37833 | 1.1664 | 5.6399 | 14.0131 | 11.2474 | 9.6978 | 2.5727 | 1.6647
Day profile:
1 | SA: 47.7826; SE: 26.9047; SE: 43.2018; SA: 5.6759; SE: 39.7578; WA: 51.3308; SE: 27.6997; WE: 15.5776; WE: 12.8361
2 | SA: 46.4662; SE: 25.244; SE: 39.9147; SA: 5.3578; SE: 34.8783; WA: 48.6183; SE: 27.4928; WE: 14.5388; WE: 15.7499
3 | SA: 51.2146; SE: 26.8797; SE: 38.9058; SA: 5.4428; SE: 32.9206; WA: 51.0417; SE: 30.2837; WE: 15.7761; WE: 19.9
4 | SA: 56.4688; SE: 22.444; SE: 38.6371; SA: 3.9818; SE: 31.3223; WA: 43.3537; SE: 22.0154; WE: 13.0622; WE: 16.7587
5 | SA: 57.88; SE: 22.0388; SE: 42.208; SA: 3.0807; SE: 31.6025; WA: 43.2815; SE: 19.4729; WE: 12.1683; WE: 14.458
6 | SA: 61.0194; SE: 22.743; SE: 52.7878; SA: 4.1411; SE: 36.5111; WA: 44.9801; SE: 19.4609; WE: 12.1635; WE: 13.2525
7 | SA: 61.9887; SE: 26.502; SE: 68.2663; SA: 6.494; SE: 45.4728; WA: 54.41; SE: 21.8827; WE: 14.4537; WE: 12.6121
8 | SA: 62.6939; SE: 33.8437; SE: 86.7043; SA: 8.8994; SE: 51.0743; WA: 60.3029; SE: 23.8488; WE: 15.3766; WE: 11.8228
9 | SA: 62.8955; SE: 35.7862; SE: 94.3443; SA: 11.4165; SE: 55.7993; WA: 58.3235; SE: 25.4691; WE: 14.5597; WE: 10.2722
10 | SA: 62.0186; SE: 37.3939; SE: 101.2636; SA: 13.1927; SE: 59.9897; WA: 60.1379; SE: 29.4812; WE: 14.6186; WE: 11.2876
11 | SA: 64.9509; SE: 39.9942; SE: 108.2101; SA: 17.8679; SE: 63.2941; WA: 66.0992; SE: 33.9563; WE: 15.2236; WE: 10.3857
12 | SA: 68.4787; SE: 41.3379; SE: 114.3414; SA: 26.6591; SE: 68.258; WA: 71.3514; SE: 37.4029; WE: 16.1072; WE: 8.8223
13 | SA: 70.8377; SE: 42.7245; SE: 115.1168; SA: 28.2064; SE: 71.8788; WA: 77.1671; SE: 39.9732; WE: 16.9297; WE: 7.9805
14 | SA: 71.8409; SE: 43.825; SE: 116.28; SA: 28.927; SE: 77.5358; WA: 83.1851; SE: 41.6273; WE: 17.5757; WE: 8.6046
15 | SA: 75.5; SE: 46.8147; SE: 113.9871; SA: 32.8; SE: 80.7021; WA: 85.7543; SE: 42.6872; WE: 18.3619; WE: 9.4789
16 | SA: 74.9101; SE: 44.9235; SE: 109.9468; SA: 32.2126; SE: 83.045; WA: 91.7207; SE: 42.9178; WE: 21.1335; WE: 9.0831
17 | SA: 67.8096; SE: 46.8854; SE: 106.636; SA: 32.2716; SE: 88.1048; WA: 95.66; SE: 41.5897; WE: 23.3837; WE: 9.213
18 | SA: 66.1136; SE: 47.64; SE: 95.092; SA: 31.4817; SE: 89.88; WA: 94.6896; SE: 41.8635; WE: 24.498; WE: 10.3852
19 | SA: 64.8457; SE: 47.3638; SE: 90.9587; SA: 31.1442; SE: 88.0002; WA: 90.314; SE: 39.1807; WE: 25.4; WE: 12.9161
20 | SA: 65.9338; SE: 47.1874; SE: 87.2398; SA: 28.4138; SE: 83.764; WA: 86.9625; SE: 44.1; WE: 24.3631; WE: 12.8241
21 | SA: 65.4756; SE: 44.1077; SE: 84.5688; SA: 25.016; SE: 79.1442; WA: 77.5575; SE: 41.8488; WE: 22.4518; WE: 11.7802
22 | SA: 63.7475; SE: 39.2426; SE: 78.0573; SA: 21.9624; SE: 68.8687; WA: 66.2963; SE: 38.7172; WE: 20.2686; WE: 9.873
23 | SA: 63.4867; SE: 32.8632; SE: 63.8434; SA: 18.2585; SE: 55.8085; WA: 57.416; SE: 32.3763; WE: 17.5976; WE: 9.0438
24 | SA: 66.5679; SE: 29.6462; SE: 57.5185; SA: 16.3906; SE: 46.8113; WA: 54.0198; SE: 29.0931; WE: 16.0385; WE: 9.0626
General outputs:
Average depreciation ($) | SA: 268404.455; SE: 91704.8554; SE: 100651.6706; SE: 246037.4171; SE: 89468.1517; SE: 346689.0877; SE: 38023.9645; SE: 67101.1137; SE: 134202.2275; SE: 626277.0616; SE: 89468.1517; SE: 22367.0379; SE: 134202.2275; SE: 138675.6351; SE: 80521.3365; SA: 111835.1896; SE: 17893.6303; SE: 178936.3033

## SA
Location and network constraint information:
Display name | Monash TS | Hummocks TS | Mt Barker S TS | Clare ZS
Short name | Riverlands | Hummocks | Mount Barker South | Clare 33/11kV
Full name | Riverlands (Monash BSP) | Hummocks ZS | Mount Barker South BSP | Clare 33/11kV ZS
Provider | Electranet | Electranet | Electranet | Electranet
Latitude | -34.2377 | -33.7853 | -35.0848 | -33.8332
Longitude | 140.597 | 138.2035 | 138.8486 | 138.6106
Proposed network investment ($m) | 226 | 4.5 | 11 | 5
Annual network support payment ($m/yr) | 16.6322 | 0.33117 | 0.80953 | 0.36797
Commissioning year | 2022 | 2021 | 2023 | 2016
Maximum connection (MW) | 241 | 150 | 374 | 10
Maximum constraint (MVA) | 49.8426 | 28.5893 | 42.1776 | 3.24
Constraint type | Growth, None | None, Voltage | Growth, None | Growth, None
Constraint time for analysis | SA | SA | WE | SE
Max firm capacity | 95.3% | 96.5% | 82.2% | 97.5%
DNI (MJ/m2/yr) | 23.4289 | 21.7421 | 18.9047 | 21.3427
Calculated on | TS | TS | TS | ZS
Reason for exclusion
Warnings |  |  |  | No hourly data
Optimal plant
Plant size (MW) | 49.8426 | 120 | 120 | 10
Storage (hours) | 1 | 3 | 15 | 5
Firm Capacity (%) | 85.3% | 91% | 82.2% | 87.6%
Connection costs component to total plant costs ($m) | 29.2523 | 44.287 | 44.287 | 9
Total plant cost (including connection costs) ($m) | 228.7885 | 546.7308 | 762.6102 | 112.91
Cost per MW ($m/MW) | 4.0033 | 4.187 | 5.986 | 10.391
Capacity factor (%) | 28.41% | 30.48% | 40.43% | 35.23%
Annual generation (MWh) | 124058.1623 | 320448.6777 | 424987.9209 | 30857.2111
Max connection distance (km) | 9.9685 | 24 | 24 | 2
Area required (ha) | 200.4144 | 490.4651 | 845.0467 | 63.0233
O&M ($/mWh) | 13.3142 | 11.6137 | 10.3539 | 25.4495
Annual network support payment ($m/yr) | 16.6322 | 0.33117 | 0.80953 | 0.36797
Cost gap calculation
LCOE ($) | 162.0933 | 156.6493 | 166.7007 | 336.9412
Electricity sales (ex. carbon price effect) ($) | 107.9948 | 94.0091 | 76.5088 | 63.9337
Carbon price effect ($) | 82.6448 | 72.0875 | 60.2322 | 37.3133
LRET ($) | 15.5953 | 21.7925 | 11.6234 | 50.5596
NSP contribution to LCOE ($/MWh) | 134.0676 | 1.0335 | 1.9048 | 11.9249
NET BENEFIT OR LOSS ($/MWh) | 178.2091 | 32.2732 | -16.4315 | -173.2097
Smallest viable plant size:
Plant size (MW) | 49.8426 | 28.5893 | 42.1776 | 3.24
Storage (hours) | 1 | 3 | 15 | 5
Firm Capacity (%) | 85.3% | 91% | 82.2% | 87.6%
Connection costs component to total plant costs ($m) | 29.2523 | 24.6977 | 27.6097 | 4.1222
Total plant cost (including connection costs) ($m) | 228.7885 | 175.107 | 299.7529 | 51.4713
Cost per MW ($m/MW) | 4.0033 | 5.261 | 6.4523 | 14.6139
Capacity factor (%) | 28.41% | 30.48% | 40.43% | 35.23%
Annual generation (MWh) | 124058.1623 | 76344.9764 | 149374.6147 | 9997.7364
Max connection distance (km) | 9.9685 | 5.7179 | 8.4355 | 0.648
Area required (ha) | 200.4144 | 140.4532 | 342.3101 | 28.6577
O&M ($/mWh) | 13.3142 | 15.9002 | 13.0183 | 32.5739
Annual network support payment ($m/yr) | 16.6322 | 0.33117 | 0.80953 | 0.36797
Cost gap calculation
LCOE ($) | 162.0933 | 198.1387 | 181.5441 | 470.656
Electricity sales (ex. carbon price effect) ($) | 107.9948 | 94.0091 | 76.5088 | 63.9337
Carbon price effect ($) | 82.6448 | 72.0875 | 60.2322 | 37.3133
LRET ($) | 15.5953 | 21.7925 | 11.6234 | 50.5596
NSP contribution to LCOE ($/MWh) | 134.0676 | 4.3378 | 5.4195 | 36.8052
NET BENEFIT OR LOSS ($/MWh) | 178.2091 | -5.9117 | -27.7603 | -282.0442
Largest viable plant size:
Plant size (MW) | 120 | 120 | 120 | 10
Storage (hours) | 1 | 3 | 15 | 5
Firm Capacity (%) | 85.3% | 91% | 82.2% | 87.6%
Connection costs component to total plant costs ($m) | 44.287 | 44.287 | 44.287 | 9
Total plant cost (including connection costs) ($m) | 472.5494 | 546.7308 | 762.6102 | 112.91
Cost per MW ($m/MW) | 3.5689 | 4.187 | 5.986 | 10.391
Capacity factor (%) | 28.41% | 30.48% | 40.43% | 35.23%
Annual generation (MWh) | 298680.0294 | 320448.6777 | 424987.9209 | 30857.2111
Max connection distance (km) | 24 | 24 | 24 | 2
Area required (ha) | 426.326 | 490.4651 | 845.0467 | 63.0233
O&M ($/mWh) | 10.9837 | 11.6137 | 10.3539 | 25.4495
Annual network support payment ($m/yr) | 16.6322 | 0.33117 | 0.80953 | 0.36797
Cost gap calculation
LCOE ($) | 143.616 | 156.6493 | 166.7007 | 336.9412
Electricity sales (ex. carbon price effect) ($) | 107.9948 | 94.0091 | 76.5088 | 63.9337
Carbon price effect ($) | 82.6448 | 72.0875 | 60.2322 | 37.3133
LRET ($) | 15.5953 | 21.7925 | 11.6234 | 50.5596
NSP contribution to LCOE ($/MWh) | 55.6856 | 1.0335 | 1.9048 | 11.9249
NET BENEFIT OR LOSS ($/MWh) | 118.3045 | 32.2732 | -16.4315 | -173.2097
Location and network constraint information:
Max demand (yr 10) | 159.8426 | 113.5893 | 191.1776 | 14.4
Investment trigger point (MW) | 110 | 85 | 149 | 11.16
Constraint notes | If in sufficient network capability is available in Victoria, reinforcement is required. Options range from incremental uprating of 132 kV network (~$10M) to replacement double circuit 275 kV (~$226M). Preferred option would be determined by Regulatory Investment Test for Transmission (RIT-T). | 15 Mvar 132 KV capacitor banks due to voltage drop from peak load growth. Load that impacts this constraint spread between four TS, Hummocks, Kadina East, Ardrosan West, and Dalrymple. | New 275/66kV transformer due to peak load growth | Substation constrained if 10% PoE forecast exceeds N rating or if 3.8MVA load at risk for 50% POE forecast during a contingent event.
Season to use |  |  |  | Summer
Constraint | Summer | Summer | NONE | Summer
NPV | 228.0896 | 4.4308 | 11.3548 | 4.1657
Day profile:
1 | 106.6452 | 63.3132 | 113.6576
2 | 99.7526 | 54.4609 | 90.092
3 | 93.9023 | 48.4131 | 75.0116
4 | 90.3251 | 46.5267 | 69.8565
5 | 88.5628 | 46.1452 | 69.0676
6 | 89.1788 | 47.7699 | 72.5577
7 | 99.4271 | 53.6898 | 91.1853
8 | 111.8625 | 66.9319 | 110.873
9 | 118.5426 | 79.7049 | 115.2372
10 | 127.1284 | 90.8785 | 127.0176
11 | 135.781 | 97.0276 | 137.7974
12 | 143.5519 | 104.6964 | 147.9117
13 | 150.2068 | 107.098 | 155.4122
14 | 155.4962 | 110.4513 | 167.2325
15 | 158.3132 | 111.9208 | 172.7338
16 | 159.1286 | 113.5893 | 176.5723
17 | 159.8426 | 112.6245 | 184.949
18 | 159.2152 | 111.25 | 191.1776
19 | 158.4253 | 108.8584 | 191.1025
20 | 158.9718 | 103.2891 | 180.3975
21 | 154.871 | 95.4796 | 165.4155
22 | 149.185 | 84.8324 | 145.343
23 | 137.8578 | 70.7921 | 116.2017
24 | 128.6809 | 63.6683 | 100.5793
General outputs:
Average depreciation ($) | 5054950.5686 | 100651.6706 | 246037.4171 | 111835.1896

## Qld
Location and network constraint information:
Display name | Charleville ZS | St George ZS | Roma BSP | Emerald ZS | Clermont ZS | Yarranlea ZS | Cape River ZS | Torrington ZS | Millchester BSP | Chinchilla BSP | Blackwater ZS | Dysart BSP | Warwick BSP | Stanthorpe ZS | Chinchilla Town ZS | Pampas ZS | West Warwick ZS | Clifton ZS | West Dalby ZS | Stanthorpe Town ZS | Lilyvale TS | Roma ZS | Warwick ZS | Dysart ZS | Millchester ZS | Roma E ZS | Roma W ZS | Moonstone ZS
Short name | 60007255 | 60007215 | 60025702 | 40017951 | 40000023_ZS | 60025696_ZS | 20003948 | 60025703 | 20010917 | 60025697 | 40000019 | 40000020 | 60025700 | 60025701 | 60025697_ZS | 60007229 | 60007247 | 60007249 | 60007197 | 60007222 | 40000022 | 60025702_ZS | 60025700_ZS | 40000020_ZS | 20010917_ZS | 60007250 | 60007251 | Proposed Moonstone 132/22kV (Alpha) ZS
Full name | Charleville 66/22/11 ZS | St George 66/33kV ZS | T083 Roma BSS | Emerald 66/22kV ZS | Clermont 132/22kV ZS | Yarranlea 110/33kV ZS | Cape River 66/11 kV ZS | Torrington 33/11kV ZS | Millchester 132/66kV BSP | T013 Chinchilla CHIN | Blackwater 132/11/22kV ZS | Dysart 132/66/22kV BSP | T058 Warwick | Stanthorpe 110/33kV ZS | Chinchilla Town ZS | Pampas 33/11kV ZS | West Warwick 33/11kV ZS | Clifton 33/11kV ZS | West Dalby 33/11kV ZS | Stanthorpe Town 33/11kV ZS | Lilyvale 132/66kV TS | ROMA ZS | Warwick 110/33kV ZS | Dysart ZS | Millchester 66/11kV ZS | Roma East 33/11kV ZS | Roma West 33/11kV ZS | Proposed Moonstone 132/22kV (Alpha) ZS
Provider | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon
Latitude | -26.4062 | -28.0556 | -26.5781 | -23.5362 | -22.8491 | -27.7219 | -20.4761 | -27.5564 | -20.1009 | -26.7446 | -23.5872 | -22.5476 | -28.1969 | -28.6454 | -26.7446 | -27.7519 | -28.2158 | -27.9366 | -27.1796 | -28.6489 | -23.1304 | -26.5781 | -28.1969 | -22.5476 | -20.1009 | -26.5747 | -26.571 | -23.6484
Longitude | 146.2838 | 148.6287 | 148.8399 | 148.1515 | 147.6109 | 151.5309 | 145.4659 | 151.8996 | 146.2805 | 150.6454 | 148.8251 | 148.4055 | 152.0508 | 151.917 | 150.6454 | 151.3508 | 152.0012 | 151.9379 | 151.2554 | 151.9375 | 148.4265 | 148.8399 | 152.0508 | 148.4055 | 146.2805 | 148.7988 | 148.7708 | 146.6406
Proposed network investment ($m) | 70 | 70 | 14 | 24 | 4.8 | 10 | 5.5 | 40 | 46 | 2.5 | 7.85 | 9 | 35 | 80 | 5.5 | 17 | 4.75 | 1 | 2.6 | 4.5 | 2.5 | - | - | - | - | 5.05 | 0.9 | 15
Annual network support payment ($m/yr) | 5.1516 | 5.1516 | 1.0303 | 1.7662 | 0.35325 | 0.73594 | 0.40477 | 2.9437 | 3.3853 | 0.18398 | 0.57771 | 0.66234 | 2.5758 | 5.8875 | 0.40477 | 1.2511 | 0.34957 | 0.073594 | 0.19134 | 0.33117 | [5 empty] | 0.37165 | 0.066234
Commissioning year | 2022 | 2022 | 2022 | 2020 | 2023 | 2024 | 2022 | 2021 | 2017 | 2019 | 2018 | 2015 | 2017 | 2017 | 2017 | 2019 | 2016 | 2022 | 2016 | 2017 | 2017 | - | - | - | - | 2015 | 2014 | 2017
Maximum connection (MW) | 20 | 44 | 176 | 69.8 | 20 | 30 | 20 | 55 | 74.8 | 30 | 22 | 140 | 111 | 75.8 | 15.5 | 11 | 27.7 | 7.8 | 15 | 15.2 | 264 | 176 | 111 | 20 | 15 | 15 | 5 | -
Maximum constraint (MVA) | 20 | 26.6 | 24.53 | 33.9 | 20 | 2.2 | 20 | 15.8 | 26.2 | 20 | 21.2 | 33.8 | 26.5 | 20 | 15.5 | 1.34 | 20 | 0.66 | 15 | 15 | 30.98 | - | - | - | - | 17.1 | 20 | -
Constraint type | N-1 Security of Supply | N-1 Security of Supply | Voltage | N-1 Security of Supply | N-1 Security of Supply | Growth | N-1 Security of Supply | Growth | N-1 Security of Supply | N-1 Security of Supply | N-1 Security of Supply | Growth, None | N-1 Security of Supply | N-1 Security of Supply | N-1 Security of Supply | Growth, None | N-1 Security of Supply | Voltage | N-1 Security of Supply | N-1 Security of Supply | Growth, None | None | None | None | None | N-1 Security of Supply | N-1 Security of Supply
Constraint time for analysis | WA | WE | WE | WE | WE | SE | WE | WA | WA | WE | WE | WE | WE | WE | WE | SE | WE | WE | WA | WE | SE | WE | WE | WE | WE | SE | WA | WE
Max firm capacity | 99.3% | 95.6% | 100% | 90.3% | 89.8% | 81.8% | 90.3% | 95.5% | 90.7% | 99.8% | 89.4% | 90.5% | 94.4% | 94% | 99.8% | 81.1% | 94.7% | 94.2% | 96.5% | 93.6% | 79.5% | 100% | 94.4% | 90.5% | 90.5% | 89.2% | 100% | 96.9%
DNI (MJ/m2/yr) | 25.1199 | 24.8077 | 24.3391 | 24.0695 | 23.7395 | 21.8684 | 24.1052 | 21.1727 | 23.2597 | 23.3992 | 24.0945 | 22.9421 | 21.1678 | 20.1692 | 23.3991 | 22.2402 | 21.2741 | 21.279 | 22.0263 | 19.9855 |  | 24.3391 | 21.1678 | 22.9421 | 23.2597 | 24.3249 | 24.315 | 25.028
Calculated on | ZS | ZS | TS | ZS | ZS | ZS | ZS | ZS | TS | TS | ZS | TS | TS | TS | ZS | ZS | ZS | ZS | ZS | ZS
Reason for exclusion | [20 empty] | Firm Capacity too low: 0.795 | Asset: Insufficient information | Asset: Insufficient information | Asset: Insufficient information | Asset: Insufficient information | Asset: No plant configuration can meet the constraint | Asset: No plant configuration can meet the constraint | Asset: Insufficient information
Warnings |  |  |  |  | No hourly data | No hourly data | [7 empty] | Recorded peak in Morning | No hourly data | Recorded peak in Morning | Recorded peak in Morning |  |  | Recorded peak in Morning |  | No hourly data | No hourly data | No hourly data | No hourly data | Recorded peak in Night |  | No hourly data
Optimal plant
Plant size (MW) | 20 | 26.6 | 120 | 69.8 | 20 | 30 | 20 | 55 | 74.8 | 30 | 22 | 120 | 111 | 20 | 15.5 | 11 | 27.7 | 7.8 | 15 | 15.2
Storage (hours) | 3 | 3 | 5 | 5 | 5 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 10 | 15 | 15 | 15 | 15
Firm Capacity (%) | 90.7% | 85.8% | 92.1% | 84.4% | 82.7% | 80.7% | 85.6% | 89.7% | 88.6% | 89.8% | 84.4% | 82.7% | 84.6% | 81.7% | 99.8% | 80.2% | 94.7% | 94.2% | 96.5% | 93.6%
Connection costs component to total plant costs ($m) | 12 | 24.2714 | 44.287 | 33.5291 | 12 | 25 | 12 | 30.3575 | 34.6006 | 25 | 12.4125 | 44.287 | 42.3583 | 12 | 10.8968 | 9.4125 | 24.5071 | 7.9247 | 10.7549 | 10.8122
Total plant cost (including connection costs) ($m) | 122.8077 | 159.5268 | 581.6977 | 402.0668 | 130.1308 | 202.1099 | 137.3155 | 315.4528 | 486.6262 | 219.895 | 177.0926 | 797.8046 | 686.3325 | 173.2923 | 191.3128 | 127.0271 | 305.2484 | 95.4202 | 195.0373 | 188.8244
Cost per MW ($m/MW) | 5.5404 | 5.0848 | 4.4784 | 5.2799 | 5.9065 | 5.9037 | 6.2658 | 5.1836 | 6.0431 | 6.4965 | 7.4855 | 6.2793 | 5.8016 | 8.0646 | 11.6397 | 10.6922 | 10.1351 | 11.2174 | 12.2855 | 11.7113
Capacity factor (%) | 42.45% | 41.17% | 47.25% | 46.02% | 44.55% | 47.66% | 46.18% | 34.64% | 42.51% | 43.09% | 46.13% | 41.2% | 34.63% | 31.4% | 62.8% | 49.43% | 51% | 51.02% | 54.9% | 44.95%
Annual generation (MWh) | 74364.5152 | 95924.6488 | 496670.6192 | 281363.4117 | 78054.0426 | 125249.0676 | 80902.3816 | 166911.421 | 278515.1891 | 113240.7264 | 88899.692 | 433122.0118 | 336694.0348 | 55010.2548 | 85273.2591 | 47629.0198 | 123742.2565 | 34861.073 | 72134.5517 | 59846.0322
Max connection distance (km) | 4 | 5.32 | 24 | 13.96 | 4 | 6 | 4 | 11 | 14.96 | 6 | 4.4 | 24 | 22.2 | 4 | 3.1 | 2.2 | 5.54 | 1.56 | 3 | 3.04
Area required (ha) | 102.5337 | 131.7479 | 539.4778 | 341.3821 | 112.78 | 211.992 | 112.78 | 276.7815 | 362.5688 | 161.2483 | 122.5768 | 539.4778 | 506.3516 | 112.78 | 141.8373 | 89.474 | 235.2987 | 81.303 | 137.9428 | 139.5012
O&M ($/mWh) | 16.2616 | 15.277 | 10.9837 | 13.7867 | 15.3293 | 13.1741 | 16.2616 | 13.7776 | 15.6788 | 17.4417 | 19.5824 | 15.4005 | 14.3804 | 20.9301 | 22.1317 | 21.7277 | 20.3599 | 19.9857 | 23.2871 | 22.2266
Annual network support payment ($m/yr) | 5.1516 | 5.1516 | 1.0303 | 1.7662 | 0.35325 | 0.73594 | 0.40477 | 2.9437 | 3.3853 | 0.18398 | 0.57771 | 0.66234 | 2.5758 | 5.8875 | 0.40477 | 1.2511 | 0.34957 | 0.073594 | 0.19134 | 0.33117 | [5 empty] | 0.37165 | 0.066234
Cost gap calculation
LCOE ($) | 154.0935 | 145.7048 | 111.072 | 134.9469 | 155.3245 | 143.9759 | 159.5427 | 171.7749 | 165.8061 | 176.642 | 190.9334 | 176.3275 | 191.3011 | 292.1463 | 217.8393 | 250.1483 | 230.222 | 252.1474 | 259.5993 | 297.3705
Electricity sales (ex. carbon price effect) ($) | 73.8516 | 73.8516 | 73.068 | 65.3587 | 76.0715 | 71.3655 | 73.068 | 69.0553 | 53.3351 | 61.7137 | 57.631 | 49.0726 | 53.3351 | 53.3351 | 46.2212 | 55.8995 | 43.224 | 63.3222 | 43.224 | 46.2212
Carbon price effect ($) | 62.0786 | 62.0786 | 61.42 | 51.6045 | 65.0207 | 59.8256 | 61.42 | 56.7387 | 36.4812 | 46.8055 | 41.4268 | 23.6086 | 36.4812 | 36.4812 | 31.6153 | 42.3959 | 26.5005 | 53.2277 | 26.5005 | 31.6153
LRET ($) | 15.5953 | 15.5953 | 15.5953 | 28.236 | 11.6234 | 8.744 | 15.5953 | 21.7925 | 45.8896 | 34.5705 | 40.5045 | 54.4639 | 45.8896 | 45.8896 | 45.8896 | 34.5705 | 50.5596 | 15.5953 | 50.5596 | 45.8896
NSP contribution to LCOE ($/MWh) | 69.2744 | 53.7042 | 2.0744 | 6.2775 | 4.5257 | 5.8758 | 5.0031 | 17.6366 | 12.1549 | 1.6247 | 6.4985 | 1.5292 | 7.6502 | 107.0254 | 4.7467 | 26.2675 | 2.825 | 2.1111 | 2.6526 | 5.5337
NET BENEFIT OR LOSS ($/MWh) | 66.7064 | 59.5249 | 41.0857 | 16.5298 | 1.9168 | 1.835 | -4.4563 | -6.5518 | -17.9454 | -31.9276 | -44.8726 | -47.6531 | -47.945 | -49.415 | -89.3665 | -91.015 | -107.1128 | -117.8913 | -136.6626 | -168.1107
Smallest viable plant size:
Plant size (MW) | 20 | 26.6 | 24.53 | 33.9 | 20 | 2.2 | 20 | 15.8 | 26.2 | 20 | 21.2 | 33.8 | 26.5 | 20 | 15.5 | 2 | 20 | 2 | 15 | 15
Storage (hours) | 3 | 3 | 5 | 5 | 5 | 10 | 5 | 3 | 5 | 15 | 5 | 15 | 5 | 5 | 15 | 10 | 15 | 15 | 15 | 15
Firm Capacity (%) | 90.7% | 85.8% | 92.1% | 84.4% | 82.7% | 80.7% | 85.6% | 89.1% | 88.6% | 99.8% | 84.4% | 90.5% | 84.6% | 81.7% | 99.8% | 80.2% | 94.7% | 94.2% | 96.5% | 93.6%
Connection costs component to total plant costs ($m) | 12 | 24.2714 | 12.8837 | 25.8358 | 12 | 2.4467 | 12 | 10.9798 | 24.1857 | 12 | 12.2522 | 25.8143 | 24.2499 | 12 | 10.8968 | 2.0342 | 12 | 2.0342 | 10.7549 | 10.7549
Total plant cost (including connection costs) ($m) | 122.8077 | 159.5268 | 157.3748 | 227.6749 | 130.1308 | 31.8172 | 137.3155 | 110.3427 | 218.9003 | 207.7169 | 172.7327 | 361.4158 | 220.5168 | 173.2923 | 191.3128 | 38.452 | 236.5067 | 36.4168 | 195.0373 | 187.1562
Cost per MW ($m/MW) | 5.5404 | 5.0848 | 5.8904 | 5.954 | 5.9065 | 13.3502 | 6.2658 | 6.2888 | 7.4319 | 9.7858 | 7.5698 | 9.929 | 7.4063 | 8.0646 | 11.6397 | 18.2089 | 11.2253 | 17.1913 | 12.2855 | 11.7601
Capacity factor (%) | 42.45% | 41.17% | 47.25% | 46.02% | 44.55% | 47.66% | 46.18% | 28.83% | 42.51% | 62.8% | 46.13% | 60.05% | 34.63% | 31.4% | 62.8% | 49.43% | 51% | 51.02% | 54.9% | 44.95%
Annual generation (MWh) | 74364.5152 | 95924.6488 | 101527.7524 | 136650.7114 | 78054.0426 | 9184.9316 | 80902.3816 | 39902.4687 | 97554.7855 | 110030.0698 | 85666.9759 | 177805.7129 | 80381.9092 | 55010.2548 | 85273.2591 | 8659.8218 | 89344.5896 | 8938.7367 | 72134.5517 | 59058.5844
Max connection distance (km) | 4 | 5.32 | 4.906 | 6.78 | 4 | 0.44 | 4 | 3.16 | 5.24 | 4 | 4.24 | 6.76 | 5.3 | 4 | 3.1 | 0.4 | 4 | 0.4 | 3 | 3
Area required (ha) | 102.5337 | 131.7479 | 134.8958 | 179.8016 | 112.78 | 30.6566 | 112.78 | 83.6772 | 142.9821 | 176.6605 | 118.6643 | 280.9028 | 144.431 | 112.78 | 141.8373 | 29.3046 | 176.6605 | 34.9155 | 137.9428 | 137.9428
O&M ($/mWh) | 16.2616 | 15.277 | 15.5505 | 16.1492 | 15.3293 | 23.3463 | 16.2616 | 18.1053 | 19.7283 | 19.0613 | 19.7419 | 20.3256 | 19.6792 | 20.9301 | 22.1317 | 31.5611 | 21.8652 | 26.9254 | 23.2871 | 22.2912
Annual network support payment ($m/yr) | 5.1516 | 5.1516 | 1.0303 | 1.7662 | 0.35325 | 0.73594 | 0.40477 | 2.9437 | 3.3853 | 0.18398 | 0.57771 | 0.66234 | 2.5758 | 5.8875 | 0.40477 | 1.2511 | 0.34957 | 0.073594 | 0.19134 | 0.33117 | [5 empty] | 0.37165 | 0.066234
Cost gap calculation
LCOE ($) | 154.0935 | 145.7048 | 147.1948 | 152.777 | 155.3245 | 319.1342 | 159.5427 | 248.4457 | 204.3555 | 183.5979 | 193.0243 | 194.9173 | 245.5366 | 292.1463 | 217.8393 | 420.562 | 254.303 | 382.7268 | 259.5993 | 298.5807
Electricity sales (ex. carbon price effect) ($) | 73.8516 | 73.8516 | 73.068 | 65.3587 | 76.0715 | 71.3655 | 73.068 | 69.7958 | 53.3351 | 53.4822 | 57.631 | 42.5273 | 53.3351 | 53.3351 | 46.2212 | 55.8995 | 43.224 | 63.3222 | 43.224 | 46.2212
Carbon price effect ($) | 62.0786 | 62.0786 | 61.42 | 51.6045 | 65.0207 | 59.8256 | 61.42 | 57.3471 | 36.4812 | 40.5625 | 41.4268 | 20.4596 | 36.4812 | 36.4812 | 31.6153 | 42.3959 | 26.5005 | 53.2277 | 26.5005 | 31.6153
LRET ($) | 15.5953 | 15.5953 | 15.5953 | 28.236 | 11.6234 | 8.744 | 15.5953 | 21.7925 | 45.8896 | 34.5705 | 40.5045 | 54.4639 | 45.8896 | 45.8896 | 45.8896 | 34.5705 | 50.5596 | 15.5953 | 50.5596 | 45.8896
NSP contribution to LCOE ($/MWh) | 69.2744 | 53.7042 | 10.1481 | 12.9253 | 4.5257 | 80.1244 | 5.0031 | 73.7736 | 34.7016 | 1.6721 | 6.7437 | 3.7251 | 32.0443 | 107.0254 | 4.7467 | 144.471 | 3.9126 | 8.2331 | 2.6526 | 5.6075
NET BENEFIT OR LOSS ($/MWh) | 66.7064 | 59.5249 | 13.0365 | 5.3474 | 1.9168 | -99.0746 | -4.4563 | -25.7368 | -33.948 | -53.3106 | -46.7183 | -73.7414 | -77.7864 | -49.415 | -89.3665 | -143.2252 | -130.1062 | -242.3485 | -136.6626 | -169.2471
Largest viable plant size:
Plant size (MW) | 20 | 44 | 120 | 69.8 | 20 | 30 | 20 | 55 | 74.8 | 30 | 22 | 120 | 111 | 75.8 | 15.5 | 11 | 27.7 | 7.8 | 15 | 15.2
Storage (hours) | 3 | 3 | 5 | 5 | 5 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 10 | 15 | 15 | 15 | 15
Firm Capacity (%) | 90.7% | 85.8% | 92.1% | 84.4% | 82.7% | 80.7% | 85.6% | 89.7% | 88.6% | 89.8% | 84.4% | 82.7% | 84.6% | 81.7% | 99.8% | 80.2% | 94.7% | 94.2% | 96.5% | 93.6%
Connection costs component to total plant costs ($m) | 12 | 28.0002 | 44.287 | 33.5291 | 12 | 25 | 12 | 30.3575 | 34.6006 | 25 | 12.4125 | 44.287 | 42.3583 | 34.8149 | 10.8968 | 9.4125 | 24.5071 | 7.9247 | 10.7549 | 10.8122
Total plant cost (including connection costs) ($m) | 122.8077 | 226.3404 | 581.6977 | 402.0668 | 130.1308 | 202.1099 | 137.3155 | 315.4528 | 486.6262 | 219.895 | 177.0926 | 797.8046 | 686.3325 | 492.1429 | 191.3128 | 127.0271 | 305.2484 | 95.4202 | 195.0373 | 188.8244
Cost per MW ($m/MW) | 5.5404 | 4.5077 | 4.4784 | 5.2799 | 5.9065 | 5.9037 | 6.2658 | 5.1836 | 6.0431 | 6.4965 | 7.4855 | 6.2793 | 5.8016 | 6.0334 | 11.6397 | 10.6922 | 10.1351 | 11.2174 | 12.2855 | 11.7113
Capacity factor (%) | 42.45% | 41.17% | 47.25% | 46.02% | 44.55% | 47.66% | 46.18% | 34.64% | 42.51% | 43.09% | 46.13% | 41.2% | 34.63% | 31.4% | 62.8% | 49.43% | 51% | 51.02% | 54.9% | 44.95%
Annual generation (MWh) | 74364.5152 | 158672.3514 | 496670.6192 | 281363.4117 | 78054.0426 | 125249.0676 | 80902.3816 | 166911.421 | 278515.1891 | 113240.7264 | 88899.692 | 433122.0118 | 336694.0348 | 208488.8656 | 85273.2591 | 47629.0198 | 123742.2565 | 34861.073 | 72134.5517 | 59846.0322
Max connection distance (km) | 4 | 8.8 | 24 | 13.96 | 4 | 6 | 4 | 11 | 14.96 | 6 | 4.4 | 24 | 22.2 | 15.16 | 3.1 | 2.2 | 5.54 | 1.56 | 3 | 3.04
Area required (ha) | 102.5337 | 206.3211 | 539.4778 | 341.3821 | 112.78 | 211.992 | 112.78 | 276.7815 | 362.5688 | 161.2483 | 122.5768 | 539.4778 | 506.3516 | 366.7675 | 141.8373 | 89.474 | 235.2987 | 81.303 | 137.9428 | 139.5012
O&M ($/mWh) | 16.2616 | 13.6827 | 10.9837 | 13.7867 | 15.3293 | 13.1741 | 16.2616 | 13.7776 | 15.6788 | 17.4417 | 19.5824 | 15.4005 | 14.3804 | 15.6333 | 22.1317 | 21.7277 | 20.3599 | 19.9857 | 23.2871 | 22.2266
Annual network support payment ($m/yr) | 5.1516 | 5.1516 | 1.0303 | 1.7662 | 0.35325 | 0.73594 | 0.40477 | 2.9437 | 3.3853 | 0.18398 | 0.57771 | 0.66234 | 2.5758 | 5.8875 | 0.40477 | 1.2511 | 0.34957 | 0.073594 | 0.19134 | 0.33117 | [5 empty] | 0.37165 | 0.066234
Cost gap calculation
LCOE ($) | 154.0935 | 129.3086 | 111.072 | 134.9469 | 155.3245 | 143.9759 | 159.5427 | 171.7749 | 165.8061 | 176.642 | 190.9334 | 176.3275 | 191.3011 | 218.5372 | 217.8393 | 250.1483 | 230.222 | 252.1474 | 259.5993 | 297.3705
Electricity sales (ex. carbon price effect) ($) | 73.8516 | 73.8516 | 73.068 | 65.3587 | 76.0715 | 71.3655 | 73.068 | 69.0553 | 53.3351 | 61.7137 | 57.631 | 49.0726 | 53.3351 | 53.3351 | 46.2212 | 55.8995 | 43.224 | 63.3222 | 43.224 | 46.2212
Carbon price effect ($) | 62.0786 | 62.0786 | 61.42 | 51.6045 | 65.0207 | 59.8256 | 61.42 | 56.7387 | 36.4812 | 46.8055 | 41.4268 | 23.6086 | 36.4812 | 36.4812 | 31.6153 | 42.3959 | 26.5005 | 53.2277 | 26.5005 | 31.6153
LRET ($) | 15.5953 | 15.5953 | 15.5953 | 28.236 | 11.6234 | 8.744 | 15.5953 | 21.7925 | 45.8896 | 34.5705 | 40.5045 | 54.4639 | 45.8896 | 45.8896 | 45.8896 | 34.5705 | 50.5596 | 15.5953 | 50.5596 | 45.8896
NSP contribution to LCOE ($/MWh) | 69.2744 | 32.4666 | 2.0744 | 6.2775 | 4.5257 | 5.8758 | 5.0031 | 17.6366 | 12.1549 | 1.6247 | 6.4985 | 1.5292 | 7.6502 | 28.2389 | 4.7467 | 26.2675 | 2.825 | 2.1111 | 2.6526 | 5.5337
NET BENEFIT OR LOSS ($/MWh) | 66.7064 | 54.6835 | 41.0857 | 16.5298 | 1.9168 | 1.835 | -4.4563 | -6.5518 | -17.9454 | -31.9276 | -44.8726 | -47.6531 | -47.945 | -54.5924 | -89.3665 | -91.015 | -107.1128 | -117.8913 | -136.6626 | -168.1107
Location and network constraint information:
Max demand (yr 10) | 20 | 26.6 | 103.3 | 33.9 | 20 | 27.3 | 20 | 51.7 | 26.2 | 20 | 21.2 | 94.2 | 26.5 | 20 | 15.5 | 11 | 20 | 4.9 | 15 | 15 | 170 | - | - | - | - | 17.1 | 20 | -
Investment trigger point (MW) | 20 | 20 | 78.77 | 20 | 20 | 25.1 | 20 | 35.9 | 20 | 20 | 20 | 60.4 | 20 | 20 | 15 | 9.66 | 20 | 4.24 | 15 | 15 | 139.02 | 176 | 111 | 10 | 15 | 15 | 20 | -
Constraint notes | Expected network augmentation costs ~$70m for N-1 solution for 50 year period if a demand reduction opportunity is not found to keep load <15 MVA. | Expected network augmentation costs ~$70m for N-1 solution for a 50 year period at St George, if a demand reduction opportunity is not found to keep load <15 MVA. | To allow adequate volts at Roma in 132kV line contingency, as currently may breach Security Criteria. To address feeder capacity issue in short term, network support agreement has been put in place for Roma Power Station to support the volts in the event of 132kV feeder contingency. In longer term, either: i) Evaluate non-network solutions . ii) install SVC at Roma sub by November 2022. | To provide support to distribution network & de-load existing Emerald ZS, supplied by 2 long 66kV feeders. 2 projects to ensure adequate network capacity for forecast growth: rebuild existing aged Blackwater-Emerald 66kV line as new double circuit 66kV line by 2015 to provide N-1 66kV feeder capacity, plus establish new Emerald North ZS in 2020 to relieve constrained 22kV distribution network & provide long term capacity to meet future loads. | Install 20MVA 66/22kV TF at Clermont ZS & AFLC injector connected to the 66kV bus. Required as load exceeds 15MVA & N-1 capacity of the present tertiary winding supply arrangement ($4.8m in 2023). | Works for proposed new Victoria Hills ZS attributed to Yarranlea ZS. The timing is uncertain at this stage. | Load west of Cape River has reached firm capacity of the 66kV regulators. Project to establish bypass & feeder tie arrangement to allow more operational flexibility, & shorter restoration times, for regulator or 66kV line outage. Work to be completed in conjunction with proposed SCADA & protection upgrade projects for Cape River ZS. Once the 66kV demand exceeds 15MVA for loads west of Cape River, security increases to N-1(b) SOS criteria. | North St BSP link to Postmans Ridge for ~$40m in 2021 | Establish 2nd single circuit 132kV line to Millchester sub including 132kV switchworks at Milchester sub to provide N-1 capacity to Millchester BSP. 2nd project to replace 34MVA 132/66kV TF at Milchester sub with 63MVA unit. Required to maintain N-1 TF capacity. Millchester 132/66kV BSP supplied by single 132kV line from Ross sub, with partial backup via 66kV line from Clare South & Stuart. Project will install a 2nd 132kV line to Millchester sub, with Ross being the preferred source. | Replace 110/33kV TF/Reg combinations with 132/33kV TF. Use ex-Roma 40MVA 132/33kV TF. TS classified as C&I & requires full N-1 TF capacity when MD is >5MVA ($2.5M in 2019). | (22kV TF Augmentation) - Install 32MVA 66/22kV TF as does not provide N-1 regulator capacity ($4m in 2018). (22kV Regulator & 66kV Switchyard Augmentation) - Perform 66kV upgrade works to cater for Powerlink TF upgrade & replace 10MVA 11/22kV regulator with 32MVA unit ($3.85m in 2020). | Install 66kV TF bay connecting Powerlinks 100MVA 3rd 132/66kV TF to Dysart ZS. Required to connect Powerlinks proposed 100MVA 3rd 132/66kV TF to the 66kV network ($1.5m in Sep 2015). Dysart 66/22kV TFs - Install 2 x 20MVA 66/22kV TFs & disconnect Powerlink QLD tertiary windings from distribution network. Carry out 66kV switchyard augmentation works associated with larger TF. Powerlink QLD replacing No1 TF with 100MVA unit & removing No2 TF. They will not allow connection of tertiary windings of new TFs to supply the Ergon distribution network. The new larger BS TF & increased 66kV demand may require augmentation to 66kV switchyard ($7.5m in Oct 2016). | Re-build Middle Ridge-Warwick 110kV Feeder 735 as new 132kV SC Oxygen line. To provide N-1 110kV fdr capacity to Warwick & Stanthorpe. | Establish new additional Warwick-Stanthorpe 110kV line (63km) and a suite of other measures to meet n-1 SOS criteria at BSP. | 33/11kV ZS & CHIN-SKID Chinchilla 33/11kV Skid Mount ZS referred to as Chinchilla (T013) 33/11kV in latest POE forecast. Chinchilla Town 33/11kV ZS has MD of >5MVA & is classified as Sig C & I sub. Therefore, requires full N-1 transformer & 33kV feeder capacity under the Security of Supply criteria. To restore compliance, proposal to establish 11kV injection point at T13 Chinchilla BSP in 2017 & de-load Chinchilla Town ZS to <5MVA. Investment attributed at Chinchilla Town ZS, as load growth has invoked investment at BSP. | Replace 33/11kV Pampas ZS with new 2 x 15MVA 66/11kV ZS (2 x T3-15). To include 66/33kV step down TF to supply 33kV feeder to Millmerran. Reason for work is Pampus is heavily loaded & aged. It is to be converted to a 66kV, in line with sub-transmission conversion plan. | Install new 33kV line from East Warwick ZS to West Warwick ZS to allow connection of new feeder, and new 33kv fdr bay at T58 Warwick, to provide N-1 capacity to West Warwick ZS. | If/when capacity, security & low voltage issues occur on subtransmission network supplying Allora, Clifton & Mt Sibley substations, the proposed longer term solution is to establish a new Clifton East 110/33kV BSP. This sub will be located east of Clifton, adjacent to the Middle Ridge-Warwick feeder 736 110kV line. This sub is to be supplied by cutting it into Feeder 736. | Install 33kV TF & feeder CBs at West Dalby ZS. This will allow T02 Dalby East to supply Central and West Dalby ZS in 33kV closed ring arrangement & provide full N-1 33kV feeder capacity to both ZS (with full N-1 TF capacity provided by load transfer & installation of 33kV TF CB). | Install 33kV & 11kV TF Circuit Breakers & additional 33kV incomer feeder bay, Increase clearances on the Pozieres 33kV line between T60 & ME2 to allow operation at 75oC. Linked to Stanthorpe requirements for n-1. | Upgrade 66kV switchyard to cater for Powerlink TF upgrade. Linked to works at Dysart BBS/ZS. | NOTE: POE forecast is the addition of ROMA (T083) 132/33kV ROMA and ROMA (T083) 132/66kV ROMA |  |  | Investment at bulk supply point | Roma East and Roma West 33/11kV ZS classified as Sig C & I ZS, & have MDs of >5MVA but netiher complies N-1 Security of Supply criteria. Project to rebuild aged & poor condition of Roma West 2 x 2.5MVA sub into a 2 x 10MVA in 2014. A suite of projects are included to remove overloads and restore compliance with the criteria. | Roma East and Roma West 33/11kV ZS classified as Sig C & I ZS, & have MDs of >5MVA but netiher complies N-1 Security of Supply criteria. Project to rebuild aged & poor condition of Roma West 2 x 2.5MVA sub into a 2 x 10MVA in 2014. A suite of projects are included to remove overloads and restore compliance with the criteria. | Establish new ZS due to expected significant demand growth from mining activities. Exisitng network has very limited capacity & presently usesi diesel generator to supply peak loads. For the shorter term, further refinement of the generator solution has been undertaken (including better control & monitoring via SCADA). In the longer term, a better solution may be to establish a 132/22kV ZS near the existing 132kV line from Clermont to Barcaldine and establish 22kV feeders out of this new ZS to supply the Alpha area.
Season to use
Constraint | NONE | Winter | BOTH (Summer) | BOTH | NONE | Summer | NONE | BOTH (Winter) | BOTH | BOTH | NONE | BOTH | BOTH | NONE | NONE | Summer | NONE | Winter | NONE | NONE | Summer |  |  |  |  | Summer | NONE
NPV | 70.6472 | 70.6472 | 14.1294 | 22.9989 | 4.9548 | 10.5376 | 5.5509 | 39.3851 | 39.9129 | 2.3252 | 7.0645 | 7.1658 | 30.3685 | 69.4137 | 4.7722 | 15.8117 | 3.9574 | 1.0092 | 2.1662 | 3.9045 | 2.1692 | - | - | - | - | 4.0208 | 0.681 | 13.0151
Day profile:
1 | 11.6073 | 22.465 | 54.1893 | 18.1945 |  |  | 7.8182 | 23.7163 | 15.5775 | 11.6438 | 15.6857 | 74.4378 | 18.526 | 17.4956 |  | 7.8776 | 11.344 | 2.3304 | 10.2464 | 13.0487 | 132.8758 |  |  |  |  | 5.0105 | 8.2565
2 | 11.3449 | 22.097 | 49.1787 | 16.4004 |  |  | 8.6006 | 18.3796 | 13.9397 | 10.8649 | 15.5177 | 79.8056 | 15.8566 | 14.6085 |  | 7.4954 | 8.9993 | 1.8843 | 10.1479 | 10.8285 | 120.7813 |  |  |  |  | 4.5464 | 8.7315
3 | 10.8645 | 21.9434 | 47.3746 | 16.8903 |  |  | 7.4127 | 16.8566 | 13.1793 | 9.3859 | 17.317 | 78.0448 | 13.6919 | 12.9877 |  | 7.5193 | 7.6594 | 1.6088 | 10.3773 | 9.4999 | 106.4561 |  |  |  |  | 4.3663 | 9.3107
4 | 10.6589 | 21.4539 | 47.4891 | 15.7034 |  |  | 7.4871 | 16.2496 | 13.0516 | 8.6733 | 15.9979 | 83.7065 | 12.7191 | 11.9732 |  | 7.5189 | 7.3929 | 1.4721 | 10.559 | 8.6712 | 121.5797 |  |  |  |  | 4.2893 | 9.6765
5 | 10.6554 | 20.3978 | 48.3795 | 15.5687 |  |  | 5.3733 | 16.2786 | 13.1842 | 8.5595 | 17.2565 | 86.5754 | 12.5554 | 11.6866 |  | 7.6771 | 7.3012 | 1.5751 | 10.7763 | 8.3843 | 111.226 |  |  |  |  | 4.228 | 9.7271
6 | 10.6802 | 19.722 | 51.4857 | 15.1642 |  |  | 5.9228 | 17.4314 | 13.2715 | 9.3583 | 16.9283 | 87.8904 | 13.3289 | 11.9665 |  | 8.009 | 7.9505 | 1.8029 | 11.0773 | 8.6256 | 117.9494 |  |  |  |  | 4.3167 | 10.0507
7 | 10.9381 | 19.2878 | 58.1277 | 15.3322 |  |  | 6.6424 | 22.5356 | 13.5141 | 11.2883 | 16.9465 | 78.9205 | 15.871 | 13.5237 |  | 8.679 | 9.541 | 2.3547 | 11.3866 | 9.8582 | 110.9892 |  |  |  |  | 4.5239 | 10.9554
8 | 11.2809 | 20.6256 | 73.0729 | 18.5626 |  |  | 8.5326 | 34.859 | 14.2441 | 14.2248 | 15.8707 | 80.933 | 20.5706 | 17.2409 |  | 8.9725 | 12.0916 | 3.1133 | 11.72 | 12.743 | 105.8447 |  |  |  |  | 5.2474 | 12.6667
9 | 12.0652 | 22.2247 | 84.7538 | 21.4852 |  |  | 9.654 | 39.2188 | 15.2439 | 16.0918 | 16.7327 | 84.1975 | 23.7777 | 19.2672 |  | 9.0186 | 13.8107 | 3.8241 | 12.1912 | 14.2633 | 100.3324 |  |  |  |  | 6.3446 | 14.1602
10 | 13.3784 | 22.1798 | 83.1904 | 24.0111 |  |  | 8.9396 | 41.6646 | 18.5443 | 14.7483 | 16.1396 | 86.9136 | 23.29 | 20 |  | 9.3128 | 14.066 | 3.816 | 12.6964 | 15 | 95.7827 |  |  |  |  | 6.9807 | 16.747
11 | 14.7765 | 20.9527 | 80.7047 | 26.1635 |  |  | 8.8533 | 41.9448 | 23.7381 | 14.2871 | 15.5899 | 87.2138 | 23.1142 | 19.4398 |  | 9.0869 | 14.3186 | 4.051 | 13.1546 | 14.6237 | 101.0409 |  |  |  |  | 7.4195 | 18.6404
12 | 15.8639 | 21.3675 | 77.4033 | 27.3093 |  |  | 10.0028 | 44.8065 | 24.3816 | 14.2458 | 15.46 | 87.3225 | 22.4514 | 17.7739 |  | 9.7298 | 16.9899 | 4.1763 | 13.5537 | 13.1645 | 114.7338 |  |  |  |  | 7.7656 | 18.6464
13 | 16.9426 | 20.8208 | 75.3946 | 29.137 |  |  | 10.6827 | 48.0606 | 24.8321 | 14.7365 | 18.5082 | 84.848 | 22.073 | 16.5219 |  | 10.2275 | 20 | 3.5204 | 13.9504 | 12.2057 | 107.996 |  |  |  |  | 8.0795 | 18.7969
14 | 19.5651 | 23.044 | 74.8103 | 30.1286 |  |  | 12.7607 | 49.3794 | 25.0501 | 14.4405 | 18.948 | 83.5697 | 22.0506 | 16.2885 |  | 11 | 14.0615 | 3.6577 | 14.2384 | 11.8422 | 117.7511 |  |  |  |  | 8.2685 | 19.153
15 | 20 | 24.494 | 75.0765 | 31.162 |  |  | 12.8137 | 50.6906 | 25.8736 | 14.8443 | 19.0191 | 80.9259 | 21.4533 | 15.105 |  | 10.9369 | 11.6438 | 3.2754 | 14.6925 | 10.8839 | 126.6612 |  |  |  |  | 8.7136 | 20
16 | 19.3081 | 25.1076 | 72.4319 | 31.736 |  |  | 13.9439 | 51.7 | 26.2 | 14.9643 | 20.0926 | 87.0233 | 21.604 | 15.4061 |  | 10.7861 | 11.2625 | 3.7576 | 15 | 11.2346 | 132.1913 |  |  |  |  | 8.8538 | 19.6333
17 | 19.9632 | 24.8242 | 75.1203 | 32.6124 |  |  | 13.716 | 49.5228 | 25.8107 | 14.8838 | 19.9856 | 83.9498 | 22.2299 | 14.9057 |  | 10.2302 | 10.7193 | 4.2797 | 3.4296 | 11.0458 | 126.5154 |  |  |  |  | 9.0222 | 18.7673
18 | 19.4641 | 25.3831 | 80.8713 | 33.8714 |  |  | 13.3373 | 46.826 | 18.0647 | 16.3466 | 20.6329 | 94.2 | 23.9322 | 15.1608 |  | 9.7314 | 11.0988 | 4.5078 | 3.2703 | 11.1732 | 170 |  |  |  |  | 8.9363 | 18.3932
19 | 16.8673 | 26.6 | 96.9365 | 33.9 |  |  | 14.0237 | 41.1247 | 17.6756 | 20 | 21.2 | 87.7726 | 26.5 | 16.5449 |  | 9.0897 | 10.6378 | 4.9 | 3.4272 | 12.2841 | 147.2024 |  |  |  |  | 8.409 | 17.2976
20 | 17.6056 | 26.2591 | 103.3 | 32.9416 |  |  | 17.9137 | 41.1794 | 17.6779 | 18.7512 | 17.9164 | 85.2061 | 25.0086 | 17.0219 |  | 7.5328 | 10.7449 | 4.7358 | 3.5899 | 12.4753 | 133.8014 |  |  |  |  | 8.1722 | 15.2702
21 | 15.4579 | 24.7977 | 97.3216 | 32.7421 |  |  | 20 | 39.4096 | 18.1699 | 17.2387 | 19.1358 | 88.7806 | 23.4386 | 16.9149 |  | 7.0635 | 10.6636 | 4.4228 | 3.675 | 12.4982 | 138.7845 |  |  |  |  | 10.8691 | 11.2116
22 | 14.5784 | 24.4207 | 92.0918 | 30.3472 |  |  | 16.0772 | 37.0082 | 17.3946 | 16.371 | 18.8728 | 86.5322 | 23.2003 | 18.0803 |  | 7.6132 | 11.0663 | 4.3473 | 3.51 | 13.4484 | 133.2396 |  |  |  |  | 17.1 | 10.1581
23 | 13.1034 | 23.3982 | 81.1959 | 26.256 |  |  | 13.8178 | 33.8883 | 16.1379 | 15.1849 | 18.0239 | 82.9138 | 21.3282 | 18.2832 |  | 7.2529 | 10.8655 | 4.1586 | 3.4057 | 13.5442 | 115.3013 |  |  |  |  | 17.1 | 8.8653
24 | 12.357 | 21.653 | 68.1167 | 22.7247 |  |  | 11.9913 | 27.8874 | 14.8042 | 13.9976 | 17.3524 | 88.3181 | 19.9202 | 16.9079 |  | 6.5321 | 10.651 | 2.8689 | 3.1428 | 12.4386 | 120.9805 |  |  |  |  | 16.5689 | 7.7905
General outputs:
Average depreciation ($) | 1565692.654 | 1565692.654 | 313138.5308 | 536808.9099 | 107361.782 | 223670.3791 | 123018.7085 | 894681.5166 | 1028883.7441 | 55917.5948 | 175581.2476 | 201303.3412 | 782846.327 | 1789363.0331 | 123018.7085 | 380239.6445 | 106243.4301 | 22367.0379 | 58154.2986 | 100651.6706 | [5 empty] | 112953.5415 | 20130.3341

## NSW
Location and network constraint information:
Display name | Gunnedah supply | Beryl TS | Mudgee ZS | TWT-QDI line | GW-THA line | Bourkelands ZS | OR-BNY line | Gunnedah TS | Moree TS | Narrabri TS | Gloucester supply | Tharbogang ZS | Quirindi ZS | Blayney ZS | Orange W ZS | OR-ORW line | QBN-Googong line
Short name | GUN_NAR_MOR | BYL | MUD | TQ_STLI | GW_STLI | BOU | OR_BNY_STLI | GUN | MOR | NAR | GLC | THA | QDI | BNY | ORW | OR_STLI | GTT_STLI
Full name | Gunnedah-Narrabri- Moree supply | Beryl (aggregate of Beryl, Mudgee and Ilford) | Mudgee zone substation | Tamworth to Quirindi - new 66kV feeder | Griffith West - new dual 132kV feeder | Bourkelands | Orange to Blayney - reconductor 66kV feeder | Gunnedah Terminal Substation | Moree Terminal Substation | Narrabri Terminal Substation | STR4B6 Gloucester No | THARBOGANG 33/11 | Quirindi ZS | Blayney ZS | ORANGE WEST 66/11 | Orange N - W feeder | Googong Town to Tralee - new 132 kV feeder
Provider | Transgrid | Transgrid | Essential | Essential | Essential | Essential | Essential | Transgrid | Transgrid | Transgrid | Essential | Essential | Essential | Essential | Essential | Essential | Essential
Latitude | -30.9774 | -32.3483 | -32.5861 | -31.4942 | -34.2816 | -35.155 | -33.5663 | -30.9774 | -29.4852 | -30.317 | -32.0141 | -34.2816 | -31.4942 | -33.5663 | -33.2684 | -33.2844 | -33.4332
Longitude | 150.3397 | 149.4611 | 149.5692 | 150.6785 | 146.0019 | 147.3422 | 148.9891 | 150.3397 | 149.8555 | 149.7976 | 151.9652 | 146.0019 | 150.6785 | 148.9891 | 149.0722 | 149.0858 | 149.2078
Proposed network investment ($m) | 30 | 35 | 1.5 | 20 | 4.5 | 2 | 8 | - | - | - | 15.7 | - | - | - | - | 1.1 | 4.3
Annual network support payment ($m/yr) | 2.2078 | 2.5758 | 0.11039 | 1.4719 | 0.33117 | 0.14719 | 0.58875
Commissioning year | 2019 | 2016 | 2019 | 2017 | 2015 | 2018 | 2016 | - | - | - | 2016 | - | - | - | - | 2016 | 2018
Maximum connection (MW) | 95 | 95 | 19 | 18.6429 | 15 | 13.4833 | 17.96 | 60 | 60 | 60 | 19.5 | 12 | - | - | - | - | -
Maximum constraint (MVA) | 42.4932 | 36.3333 | 3.2 | 7.7714 | 0.58 | 7.7333 | 5.74 | - | - | - | 14.173 | - | - | - | - | - | -
Constraint type | Growth, Voltage | Voltage | Reliability | Growth - mine related | Growth | Growth | Growth - mine related | None, Voltage | None, Voltage | None, Voltage | Growth - mine related | Growth
Constraint time for analysis | WE | WE | WE | SE | WE | SE | WE | WE | WE | WE | SE | WE | WE | WE | WE | WE | WE
Max firm capacity | 95.1% | 87.2% | 87.8% | 82.9% | 88.5% | 88.4% | 87.8% | 95.1% | 95.3% | 92.7% | 74.1% | 88.5% | 92.6% | 87.8% | 86.7% | 86.7% | 86.7%
DNI (MJ/m2/yr) | 22.1971 | 21.4092 | 21.214 | 21.3145 | 23.3894 | 21.5803 | 20.5221 | 22.1971 | 24.0757 | 23.7595 |  | 23.3894 | 21.3145 | 20.5221 | 20.5428 | 20.4684 | 19.8397
Calculated on | Stli | TS | ZS | Stli | Stli | ZS | Stli
Reason for exclusion | [7 empty] | Asset: Insufficient information | Asset: Insufficient information | Asset: Insufficient information | Firm Capacity too low: 0.741 | Asset: Insufficient information | Asset: Insufficient information | Asset: Insufficient information | Asset: Insufficient information | Asset: Insufficient information | Asset: Insufficient information
Warnings |  |  |  | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data | No hourly data
Optimal plant
Plant size (MW) | 95 | 95 | 19 | 18.6429 | 15 | 13.4833 | 17.96
Storage (hours) | 5 | 15 | 15 | 15 | 15 | 15 | 15
Firm Capacity (%) | 80.6% | 87.2% | 87.8% | 82.9% | 88.5% | 88.4% | 87.8%
Connection costs component to total plant costs ($m) | 38.9295 | 38.9295 | 11.778 | 11.6959 | 10.7549 | 10.2936 | 11.5344
Total plant cost (including connection costs) ($m) | 548.1405 | 859.0799 | 200.725 | 216.4832 | 202.9223 | 166.9291 | 220.0617
Cost per MW ($m/MW) | 5.3601 | 8.6332 | 9.9446 | 10.9848 | 12.8112 | 11.617 | 11.6106
Capacity factor (%) | 38.3% | 51.68% | 50.7% | 51.2% | 62.74% | 52.55% | 47.37%
Annual generation (MWh) | 318747.2787 | 430041.4329 | 84378.3637 | 83612.0902 | 82443.9377 | 62067.6515 | 74530.9803
Max connection distance (km) | 19 | 19 | 3.8 | 3.7286 | 3 | 2.6967 | 3.592
Area required (ha) | 444.8835 | 696.8726 | 168.9573 | 166.2013 | 137.9428 | 126.0988 | 160.9246
O&M ($/mWh) | 13.5505 | 15.5438 | 19.2766 | 21.2547 | 24.2835 | 21.7988 | 22.3865
Annual network support payment ($m/yr) | 2.2078 | 2.5758 | 0.11039 | 1.4719 | 0.33117 | 0.14719 | 0.58875
Cost gap calculation
LCOE ($) | 161.3242 | 191.9561 | 226.4122 | 247.8128 | 239.8924 | 255.2363 | 281.1909
Electricity sales (ex. carbon price effect) ($) | 62.1697 | 41.2565 | 51.9464 | 44.4439 | 40.6244 | 48.4438 | 41.2565
Carbon price effect ($) | 46.5558 | 28.3487 | 38.9 | 32.1367 | 22.8615 | 34.9881 | 28.3487
LRET ($) | 34.5705 | 50.5596 | 34.5705 | 45.8896 | 54.4639 | 40.5045 | 50.5596
NSP contribution to LCOE ($/MWh) | 6.9265 | 5.9896 | 1.3083 | 17.6036 | 4.0169 | 2.3714 | 7.8994
NET BENEFIT OR LOSS ($/MWh) | -11.1017 | -65.8017 | -99.687 | -107.739 | -117.9257 | -128.9285 | -153.1267
Smallest viable plant size:
Plant size (MW) | 42.4932 | 36.3333 | 3.2 | 7.7714 | 2 | 7.7333 | 5.74
Storage (hours) | 5 | 10 | 15 | 15 | 15 | 15 | 15
Firm Capacity (%) | 80.6% | 81.4% | 87.8% | 82.9% | 88.5% | 88.4% | 87.8%
Connection costs component to total plant costs ($m) | 27.6773 | 26.3572 | 4.0684 | 7.9088 | 2.0342 | 7.8875 | 6.5974
Total plant cost (including connection costs) ($m) | 283.3327 | 333.2018 | 59.7121 | 120.2401 | 50.2429 | 114.8414 | 101.9151
Cost per MW ($m/MW) | 6.0164 | 8.4453 | 17.3887 | 14.4544 | 24.1043 | 13.8302 | 16.6059
Capacity factor (%) | 38.3% | 45.56% | 50.7% | 51.2% | 62.74% | 52.55% | 47.37%
Annual generation (MWh) | 142574.6543 | 145015.5213 | 14211.0928 | 34854.3886 | 10992.525 | 35598.7519 | 23820.0349
Max connection distance (km) | 8.4986 | 7.2667 | 0.64 | 1.5543 | 0.4 | 1.5467 | 1.148
Area required (ha) | 219.9901 | 251.4723 | 44.5687 | 81.0762 | 34.9155 | 80.7737 | 64.9052
O&M ($/mWh) | 16.1613 | 19.1855 | 28.4741 | 25.7441 | 37.7528 | 24.621 | 28.7394
Annual network support payment ($m/yr) | 2.2078 | 2.5758 | 0.11039 | 1.4719 | 0.33117 | 0.14719 | 0.58875
Cost gap calculation
LCOE ($) | 182.0277 | 214.912 | 390.6621 | 323.8628 | 443.4233 | 302.5331 | 398.8887
Electricity sales (ex. carbon price effect) ($) | 62.1697 | 43.5539 | 51.9464 | 44.4439 | 40.6244 | 48.4438 | 41.2565
Carbon price effect ($) | 46.5558 | 29.9273 | 38.9 | 32.1367 | 22.8615 | 34.9881 | 28.3487
LRET ($) | 34.5705 | 50.5596 | 34.5705 | 45.8896 | 54.4639 | 40.5045 | 50.5596
NSP contribution to LCOE ($/MWh) | 15.4853 | 17.7621 | 7.7679 | 42.2292 | 30.127 | 4.1346 | 24.7166
NET BENEFIT OR LOSS ($/MWh) | -23.2464 | -73.109 | -257.4774 | -159.1634 | -295.3466 | -174.4621 | -254.0073
Largest viable plant size:
Plant size (MW) | 95 | 95 | 19 | 18.6429 | 15 | 13.4833 | 17.96
Storage (hours) | 5 | 15 | 15 | 15 | 15 | 15 | 15
Firm Capacity (%) | 80.6% | 87.2% | 87.8% | 82.9% | 88.5% | 88.4% | 87.8%
Connection costs component to total plant costs ($m) | 38.9295 | 38.9295 | 11.778 | 11.6959 | 10.7549 | 10.2936 | 11.5344
Total plant cost (including connection costs) ($m) | 548.1405 | 859.0799 | 200.725 | 216.4832 | 202.9223 | 166.9291 | 220.0617
Cost per MW ($m/MW) | 5.3601 | 8.6332 | 9.9446 | 10.9848 | 12.8112 | 11.617 | 11.6106
Capacity factor (%) | 38.3% | 51.68% | 50.7% | 51.2% | 62.74% | 52.55% | 47.37%
Annual generation (MWh) | 318747.2787 | 430041.4329 | 84378.3637 | 83612.0902 | 82443.9377 | 62067.6515 | 74530.9803
Max connection distance (km) | 19 | 19 | 3.8 | 3.7286 | 3 | 2.6967 | 3.592
Area required (ha) | 444.8835 | 696.8726 | 168.9573 | 166.2013 | 137.9428 | 126.0988 | 160.9246
O&M ($/mWh) | 13.5505 | 15.5438 | 19.2766 | 21.2547 | 24.2835 | 21.7988 | 22.3865
Annual network support payment ($m/yr) | 2.2078 | 2.5758 | 0.11039 | 1.4719 | 0.33117 | 0.14719 | 0.58875
Cost gap calculation
LCOE ($) | 161.3242 | 191.9561 | 226.4122 | 247.8128 | 239.8924 | 255.2363 | 281.1909
Electricity sales (ex. carbon price effect) ($) | 62.1697 | 41.2565 | 51.9464 | 44.4439 | 40.6244 | 48.4438 | 41.2565
Carbon price effect ($) | 46.5558 | 28.3487 | 38.9 | 32.1367 | 22.8615 | 34.9881 | 28.3487
LRET ($) | 34.5705 | 50.5596 | 34.5705 | 45.8896 | 54.4639 | 40.5045 | 50.5596
NSP contribution to LCOE ($/MWh) | 6.9265 | 5.9896 | 1.3083 | 17.6036 | 4.0169 | 2.3714 | 7.8994
NET BENEFIT OR LOSS ($/MWh) | -11.1017 | -65.8017 | -99.687 | -107.739 | -117.9257 | -128.9285 | -153.1267
Location and network constraint information:
Max demand (yr 10) | 137.4932 | 131.3333 | 22.2 | 26.4143 | 17.9 | 21.2167 | 23.7 | - | - | - | 34.225 | - | - | - | - | - | -
Investment trigger point (MW) | 95 | 95 | 19 | 18.6429 | 17.32 | 13.4833 | 17.96 | 60 | 60 | 60 | 20.052 | 12 | - | - | - | - | -
Constraint notes | New supply to Gunnedah-Moree-Narrabri area. Assumes 2 hot spots. | This is aggregaate demand for Transgrid & Essential loads at Beryl, Mudgee & Ilford. |  |  |  | Peak demand on ZS expected to exceed summer rating in 2017/18 | Blaney area supplied at 66kV from Bathurst. Existing load approaching 15kV with projected increase associated with mining. Should this eventuate & N-1 reliability be required, alternative 66kV feed from Orange would need to be augmented. | Voltage support required for supply to Gunnedah-Moree-Narrabri area; 100% value if provided here | Voltage support required for supply to Gunnedah-Moree-Narrabri area; 80% value if provided here | Voltage support required for supply to Gunnedah-Moree-Narrabri area; 80% value if provided here | Load & forecast for GLC AREA, not ZS used. Existing 33kV network has N-1 capacity of 19.5MVA. Current peak demand ~12MVA & new 7MVA mining load projected. Unacceptable overload in N-1 conditions.
Season to use
Constraint | BOTH | BOTH (Summer) | BOTH (Winter) | Summer | Winter | Summer | Winter |  |  |  | Summer
NPV | 27.903 | 29.16 | 1.3951 | 17.3534 | 3.5829 | 1.7999 | 6.6651 | - | - | - | 13.0803 | - | - | - | - | 0.91646 | 3.8697
Day profile:
1 | 112.1739 | 84.8714 | 11.7115
2 | 112.7825 | 84.7265 | 10.9773
3 | 104.0616 | 82.6319 | 10.2673
4 | 89.7326 | 81.9639 | 10.0288
5 | 88.667 | 82.1812 | 10.2432
6 | 93.1485 | 85.6461 | 10.7068
7 | 108.7274 | 91.3585 | 11.7524
8 | 126.0328 | 98.1132 | 13.9178
9 | 129.4249 | 101.238 | 16.9561
10 | 122.9825 | 99.9321 | 17.2398
11 | 117.1569 | 98.0971 | 16.2853
12 | 111.7343 | 93.5638 | 15.7252
13 | 107.2526 | 90.95 | 15.3143
14 | 103.5848 | 91.3263 | 14.5985
15 | 101.0825 | 97.1373 | 15.0086
16 | 102.3541 | 96.3727 | 15.3759
17 | 106.3482 | 106.6325 | 17.0283
18 | 123.5808 | 127.3272 | 21.2937
19 | 137.4932 | 131.3333 | 22.2
20 | 131.984 | 126.9509 | 21.0964
21 | 124.4953 | 113.2866 | 19.2864
22 | 116.6323 | 116.9245 | 17.143
23 | 117.3089 | 123.8341 | 14.8559
24 | 115.6634 | 114.7373 | 13.2784
General outputs:
Average depreciation ($) | 671011.1374 | 782846.327 | 33550.5569 | 447340.7583 | 100651.6706 | 44734.0758 | 178936.3033